## Rev 3
Level 1 | Level 2 | Level 3 | Level 4 | Level 5 | Level 6
|  | default setting | default setting | default setting | default setting | setting range/alternate text indication |  |  |  |  | condition(s) for parameter to be displayed | parameter description and comments | parameter long name
Status | Unit-S | Unit-S Off-Idle
| Econ-S | Econ-S Disabled
| ExF-S | ExF-S Off-Idle
| Fan-S | Fan-S Off-Idle
| Clg-S | Clg-S Off-Idle
| Htg-S | Htg-S Off-Disabled
| HGR-S | HGR-S Off-Disabled
| Dvent-Mode | Dvent-Mode Disabled |  |  |  | controlled by IAQ | Difference between IAQ and OAQ |  |  |  | economizer board present | Demand Ventilation mode selection; Disabled permits no demand ventilation function. Controlled by IAQ requires IAQ input. Diff between IAQ and OAQ requires IAQ and OAQ inputs.
| OprST | OprST 70.1 F | [9 empty] | The buffered space temperature in use; may be from UCB RAT thermistor or ST thermistor input, SA BUS NetSensor or FC BUS communicated value sources.
| SAT | SAT 60.6 F | [9 empty] | The buffered UCB SAT thermistor input.
| RAT | RAT 70.1 F | [9 empty] | The buffered UCB RAT thermistor input.
| OprSH | OprSH 30.2 %H |  |  |  | Input Unreliable |  |  |  |  | input to the UCB RAH pins, humidity from NetSensor or communicated value | The buffered space humidity in use; may be from UCB RAH 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value source; Input Unreliable indicates RAH input was once detected and is currently lost.
| RAH | RAH 50 %H |  |  |  | Out of range low |  |  |  |  | input to the UCB RAH pins | The buffered UCB RAH 0-10 VDC input; Out of range low indicates UCB RAH 0-10 VDC input was once detected and is currently lost.
| OprOAT | OprOAT 70.0 F |  |  |  | Input Unreliable | [5 empty] | The buffered outdoor air temperature in use; may be from UCB OAT thermistor input or FC BUS communicated value sources.
| OprOAQ | OprOAQ 195ppm |  |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered outdoor air quality in use; may be from economizer board OAQ 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAQ input is currently not present.
| OprIAQ | OprIAQ 488ppm |  |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered indoord air quality in use; may be from economizer board IAQ 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; Input Unreliable indicates IAQ input is currently not present.
| OprOAH | OprOAH 50 %H |  |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present.
Alarms | No Events | [9 empty] | No alarms in the active alarm register. | No notification in the active alarm register.
| Alarm Desription | [9 empty] | 1 or more alarms in the active alarm register. | Most recent notification in the active alarm register.
| Alarm Desription | [9 empty] | 2 or more alarms in the active alarm register. | 2nd most recent notification in the active alarm register.
| Alarm Desription | [9 empty] | 3 or more alarms in the active alarm register. | 3rd most recent notification in the active alarm register.
| Alarm Desription | [9 empty] | 4 or more alarms in the active alarm register. | 4th most recent notification in the active alarm register.
| Alarm Desription | [9 empty] | 5 or more alarms in the active alarm register. | 5th most recent notification in the active alarm register.
Summary | HVACZone | OccSrc | OccSrc Local Schedule |  |  | BAS Network Req | [5 empty] | The source of occupied/unoccupied status; Local input is 24 VAC input to the UCB OCC terminal, (Schedule is from the UCB schedule), BAS Network Req is from FC BUS communicated value
|  | OprCVClg-Sp | OprCVClg-Sp 85 F | [7 empty] | FanCtl-Type ≠ Variable Speed | Effective if TSTstatTAT-Only = No; the CV cooling setpoint in use; depending on occupied/unoccupied status, is either ClgOcc-Sp ± OprSSO or ClgUnocc-Sp ± OprSSO; cooling operation requests are initiated when OprST rises above this setpoint
|  | CVOprHtg-Sp | CVOprHtg-Sp 60 F | [7 empty] | FanCtl-Type ≠ Variable Speed | Effective if TSTstatTAT-Only = No; the CV heating setpoint in use; depending on occupied/unoccupied status, is either CVHtgOcc-Sp ± OprSSO or CVHtgUnocc-Sp ± OprSSO; heating operation requests are initiated when OprST falls below this setpoint
|  | OprVAVClg-Sp | OprVAVClg-Sp 85 F | [7 empty] | FanCtl-Type ≠ Variable Speed | The VAV cooling SAT setpoint in use; with OprST above SATRst-Sp is SATLo-Sp, with OprST below SATRst-Sp is SATUp-Sp; cooling operation requests are initiated when OprST rises above this setpoint
|  | VAVOprHtg-Sp | VAVOprHtg-Sp 60 F | [7 empty] | FanCtl-Type ≠ Variable Speed | The VAV space heating setpoint in use; depending on occupied/unoccupied status and enabled VAV heating modes, is either MornWRAT-Sp or VAVHtgUnocc-Sp or VAVHtgOcc-SP; heating operation requests are initiated when OprST falls below this setpoint
|  | OprSZVAVClg-Sp | OprSZVAVClg-Sp 72 F | [7 empty] | SZVAVEn = On | Effective for SZ VAV units; the single zone VAV space setpoint in use
|  | OprST | OprST 70.1 F | [8 empty] | The buffered space temperature in use; may be from UCB RAT thermistor or ST thermistor input, SA BUS NetSensor or FC BUS communicated value sources
|  | OprSH | OprSH 19.5 %H |  |  | Input Unreliable |  |  |  |  | input to the UCB RAH pins, humidity from NetSensor or communicated value | The buffered space humidity in use; may be from UCB RAH 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates RAH input was once detected and is currently lost
|  | OprIAQ | OprIAQ 488ppm |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered indoor air quality in use; may be from economizer board IAQ 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates IAQ input is currently not present
| Fan | Fan | Fan Off |  |  | On | [5 empty] | UCB FAN 24 VAC output status
|  | FanCtl-Type | FanCtl-Type Single Speed |  |  | Two Speed | Fixed Variable | Variable Speed |  |  |  | Indoor blower and unit operating mode selection; Single Speed = CV unit w/o indoor blower VFD, (Two Speed = CV unit w/2-step indoor blower VFD speed control), Fixed Variable = CV unit w/IntelliSpeed indoor blower VFD speed control, Variable Speed = VAV unit w/indoor blower VFD speed control by DCT PRS input
|  | FanVFD | FanVFD 0 % | [7 empty] | FanCtl-Type ≠ Single Speed | UCB VFD 2-10 VDC output status
|  | DctPrs-Sp | DctPrs-Sp 1.50"/w |  |  | .00"/w | through | 4.33"/w |  |  | FanCtl-Type ≠ Variable Speed | Effective for VAV units; supply duct pressure setpoint for indoor blower speed control; 1/100th adjustment increments
|  | DctPrs | DctPrs .90"/w | [7 empty] | FanCtl-Type ≠ Variable Speed | Effective for VAV units; the buffered UCB DCT PRS 0-5 VDC input
|  | FanOnOcc | FanOnOcc Yes |  |  | No | [5 empty] | effective for CV units; Yes = UCB FAN output is on during occupied status, cycles with heating/cooling operation and fan request during unoccupied status; No = UCB FAN output cycles with heating/cooling operation and fan request
| Clg | C1 | C1 Off |  |  | On | [5 empty] | UCB C1 24 VAC output status
|  | C2 | C2 Off |  |  | On |  |  |  |  | #ClgStgs = 2 or more | UCB C2 24 VAC output status
|  | C3 | C3 Off |  |  | On |  |  |  |  | #ClgStgs = 3 or more | UCB C3 24 VAC output status
|  | C4 | C4 Off |  |  | On |  |  |  |  | #ClgStgs = 4 or more | UCB C4 24 VAC output status
|  | StgClgCmd | StgClgCmd 0%
| Htg | H1 | H1 Off |  |  | On |  |  |  |  | #HtgStgs = 1 or more | UCB H1 24 VAC output status
|  | H2 | H2 Off |  |  | On |  |  |  |  | #HtgStgs = 2 or more | UCB H2 24 VAC output status
|  | H3 | H3 Off |  |  | On |  |  |  |  | #HtgStgs = 3 or more | UCB H3 24 VAC output status
|  | HWV | HWV 0 % | [7 empty] | 4-stage board present | 4-stage board 2-10 VDC output status
|  | StgHtgCmd | StgHtgCmd 0%
| Heat Pump | Clg-S | Clg-S Off-Idle
|  | Htg-S | Htg-S Off-Idle
|  | C1 | C1 Off |  |  | On | [5 empty] | UCB C1 24 VAC output status
|  | C2 | C2 Off |  |  | On |  |  |  |  | #ClgStgs = 2 or more | UCB C2 24 VAC output status
|  | RevVlv | RevVlv Off |  |  | On |  |  |  |  | #HtPumpStgs ≠ 0 | UCB H1 output status
|  | AuxHtg | AuxHtg Off |  |  | On |  |  |  |  | #HtPumpStgs ≠ 0 and #HtgStgs = 2 or more | UCB H2 output status
|  | Mode | Mode Cooling | [8 empty] | Heat pump mode status
| Econ | Econ-Free | Econ-Free No |  |  | Yes |  |  |  |  | economizer board present | Yes indicates economizer free cooling is available, No indicates economizer free cooling is not availble; indication depends on FreeClg-Mode effective and current outdoor/indoor conditions
|  | FreeClg-Mode | FreeClg-Mode Dry Bulb Temperature |  |  | Single Enthalpy | Dual Enthalpy |  |  |  | economizer board present | Free cooling changeover method currently effective; indication depends on FreeClg-Sel setting, presence of OAH 0-10 VDC input to the economizer board and presence of RAH 0-10 VDC input to the UCB
|  | Econ | Econ 0% | [7 empty] | economizer board present | Economizer board ECON 2-10 VDC output status
|  | LowAmb-MinPos | LowAmb-MinPos 0% |  |  | 0% | through | 100% |  |  | economizer board present | Economizer minimum position effective with occupied status, indoor blower operation and when OAT is below LowAmb-Sp; typically set less than Econ-MinPos
|  | EconOAT-SpEn | EconOAT-SpEn 55 F |  |  | 40 F | through | 80 F |  |  | economizer board present | Dry bulb free cooling changeover setpoint; with FreeClg-Mode = Dry Bulb Tempe, economizer free cooling is available when OAT is below this setpoint
|  | EconOAEnth-Sp | EconOAEnth-Sp 27 B/# |  |  | 10 B/# | through | 50 B/# |  |  | economizer board present | Single enthalpy free cooling changeover setpoint; with FreeClg-Mode = Single Enthalpy, economizer free cooling is available when OA-Enth is below this setpoint
|  | OA-Enth | OA-Enth 0B/# |  |  | 0 B/# |  |  |  |  | economizer board present | Enthalpy calculated from OAH 0-10 VDC input to the economizer board and OprOAT; 0B/# indicated if OAH 0-10 VDC input to the economizer board is not present
|  | OprOAH | OprOAH 19 %H |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; ?Unrel indicates OAH input is currently not present
|  | OprOAT | OprOAT 70.0 F | [7 empty] | economizer board present | The buffered outdoor air temperature in use; may be from UCB OAT input or communicated value sources
|  | RA-Enth | RA-Enth 0B/# |  |  | 0 B/# |  |  |  |  | economizer board present | Enthalpy calculated from RAH 0-10 VDC input to the UCB and RAT thermistor input to the UCB; 0B/# indicated if RAH 0-10 VDC input to the UCB is not present
|  | RAH | RAH 19.5 %H |  |  | Input Unreliable |  |  |  |  | economizer board present and input to the UCB RAH pins | The buffered UCB RAH 0-10 VDC input; ?Unrel indicates UCB RAH 0-10 VDC input was once detected and is currently lost
|  | RAT | RAT 70.1 F | [7 empty] | economizer board present | The buffered UCB RAT thermistor input
| Dvent | Dvent-Mode | Dvent-Mode Disabled |  |  | Controlled by IAQ | Diff between IAQ and OAQ |  |  |  | economizer board present | Demand Ventilation mode selection; Disabled permits no demand ventilation function, Controlled by IAQ requires IAQ input, Diff between IAQ and OAQ requires IAQ and OAQ inputs
|  | DVentIAQ-Sp | DVentIAQ-Sp 1000ppm |  |  | 0ppm | through | 5000ppm |  |  | economizer board present | Effective when DVent-Mode = Controlled by IAQ; with occupied status and indoor blower operation, demand ventilation operation the economizer is initiated if OprIAQ rises above this setpoint; adjustment increments of 1s
|  | DventDiff-Sp | DVentDiff-Sp 600ppm |  |  | 0ppm | through | 5000ppm |  |  | economizer board present | Effective when DVent-Mode = Diff between IAQ and OAQ; with occupied status and indoor blower operation, demand ventilation operation the economizer is initiated if OprIAQ rises above OprOAQ plus this setpoint; adjustment increments of 1s
|  | OprIAQ | OprIAQ 489ppm |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered indoor air quality in use; may be from economizer board IAQ 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates IAQ input is currently not present
|  | OprOAQ | OprOAQ 195ppm |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered outdoor air quality in use; may be from economizer board OAQ 0-10 VDC input or FC BUS communicated value sources; ?Unrel indicates OAQ input is currently not present
| PowerEx | ExFType | ExFType None |  |  | Non-Modulating | Modulating Damper | Variable Frequency Fan |  |  | economizer board present | Power exhaust fan mode selection; None = no power exhaust fan installed, Non-Modulating = power exhaust fan on/off by economizer position, (Modulating Damper = power exhaust fan on/off by exhaust damper position, exhaust damper position by BLDG PRES input), (Variable Frequency Fan = power exhaust fan VFD speed control by BLDG PRES input)
|  | ExFan | ExFan Off |  |  | On |  |  |  |  | economizer board present | Economizer board EX-FAN 24 VAC output status
|  | EAD-O | EAD-O 0 % | [7 empty] | economizer board present and ExFType = Modulating Damper | Effective for Modulating Damper power exhaust; the economizer board EX VFD 2-10 VDC output status
|  | ExFanVFD | ExFanVFD 0 % | [7 empty] | economizer board present and ExFType = Variable Frequency Fan | Effective for Variable Frequency Fan power exhaust; the economizer board EX VFD 2-10 VDC output status
|  | Bldg-Sp | Bldg-Sp .100"/w |  |  | -.249"/w | through | .249"/w |  |  | economizer board present and ExFType ≠ Non-Modulating | Effective for Modulating Damper and Variable Frequency Fan power exhaust; building pressure setpoint for exhaust damer position/exhaust fan VFD speed control; 1/100th adjustment increments
|  | BldgPres | BldgPres -.010"/w |  |  | Input Unreliable |  |  |  |  | economizer board present and ExFType ≠ Non-Modulating | Effective for Modulating Damper and Variable Frequency Fan power exhaust; the buffered economizer board BLDG PRES 0-5 VDC input; ?Unrel indicates BLDG PRS input is currently not present
|  | Econ | Econ 0% | [7 empty] | economizer board present | Economizer board ECON 2-10 VDC output status
|  | EconDmpPosFanOn | EconDmpPosFanOn 60 % |  |  | 20% | through | 99% |  |  | economizer board present and ExFType = Non-Modulating | Effective for Non-Modulating power exhaust; the Econ position where the economizer board EX-FAN 24 VAC output is turned On; must be set greater than EconDmpPosFanOff
|  | EconDmpPosFanOff | EconDmpPosFanOff 20 % |  |  | 10% | through | 89% |  |  | economizer board present and ExFType = Non-Modulating | Effective for Non-Modulating power exhaust; the Econ position where the economizer board EX-FAN 24 VAC output is turned Off; must be set greater than Econ-MinPos and less than EconDmpPosFanOff
| HGR | HGR | HGR Off |  |  | On |  |  |  |  | HGR-En = On | UCB AuxHGR status
|  | HGRHum-Sp | HGRHum-Sp 60 %H |  |  | 0 | through | 100% |  |  |  | effective for hot gas reheat operation when Occupied; hot gas reheat operation is initiated when OprSH rises above this setpoint
|  | HGRUnoccHum-SP | HGRUnoccHum-SP 70 F |  |  | 0% | through | 100% |  |  |  | effective for hot gas reheat operation when UnOccupied; hot gas reheat operation is initiated when OprSH rises above this setpoint
|  | RAH | RAH 50 %H |  |  | Input Unreliable |  |  |  |  | input to the UCB RAH pins | The buffered UCB RAH 0-10 VDC input; ?Unrel indicates UCB RAH 0-10 VDC input was once detected and is currently lost
| Sensors | SAT | SAT 60.6 F | [8 empty] | The buffered UCB SAT thermistor input
|  | RAT | RAT 70.1 F | [8 empty] | The buffered UCB RAT thermistor input
|  | RAH | RAH 50 %H |  |  | Input Unreliable |  |  |  |  | input to the UCB RAH pins | The buffered UCB RAH 0-10 VDC input; ?Unrel indicates UCB RAH 0-10 VDC input was once detected and is currently lost
|  | OprOAT | OprOAT 70.0 F | [8 empty] | The buffered outdoor air temperature in use; may be from UCB OAT thermistor input or FC BUS communicated value sources
|  | OprOAH | OprOAH 19 %H |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; ?Unrel indicates OAH input is currently not present
|  | OprOAQ | OprOAQ 195ppm |  |  | Input Unreliable |  |  |  |  | economizer board present | The buffered outdoor air quality in use; may be from economizer board OAQ 0-10 VDC input or FC BUS communicated value sources; ?Unrel indicates OAQ input is currently not present
| Network | Comm-S | Comm-S Waiting For Poll |  |  | Active | [5 empty] | Effective when an optional communcation sub-board is present; Waiting For Pol indicates FC BUS network communication is not present, Active indicates FC BUS network communication is present
Commission | HVACZone | OccMode | OccMode External |  |  | Schedule | [5 empty] | Sets occupied/unoccupied status initiation method; External permits occupied/unoccupied status initiation by 24 VAC input to the UCB OCC terminal or by FC BUS communicated value, (not to be used until schedule access provisions are made in later control revisions, Schedule permits occupied/unoccupied status initiation by the schedule held in the UCB)
|  | OffDurUnocc | OffDurUnocc Yes
| IndoorFan | FanOnOcc | FanOnOcc Yes |  |  | No |  |  |  |  | FanCtl-Type ≠ Variable Speed | Effective for CV units; Yes = UCB FAN output is on during occupied status, cycles with heating/cooling operation and fan request during unoccupied status; No = UCB FAN output cycles with heating/cooling operation and fan request
|  | DctPrs-Sp | DctPrs-Sp 1.50"/w |  |  | .00"/w | through | 4.99"/w |  |  | FanCtl-Type ≠ Variable Speed | Effective for VAV units; supply duct pressure setpoint for indoor blower speed control; 1/100th adjustment increments
|  | FanOnly-%Cmd | FanOnly-%Cmd 50 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during indoor blower-only operation
|  | 1ClgStg-%Cmd | 1ClgStg-%Cmd 70 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 1-stage cooling operation
|  | 2ClgStg-%Cmd | 2ClgStg-%Cmd 80 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 2-stage cooling operation
|  | 3ClgStg-%Cmd | 3ClgStg-%Cmd 90 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 3-stage cooling operation
|  | 4ClgStg-%Cmd | 4ClgStg-%Cmd 100 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 4-stage cooling operation
|  | 1HtgStg-%Cmd | 1HtgStg-%Cmd 100 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 1-stage heating operation
|  | 2HtgStg-%Cmd | 2HtgStg-%Cmd 100 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 2-stage heating operation
|  | 3HtgStg-%Cmd | 3HtgStg-%Cmd 100 % |  |  | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | Effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 3-stage heating operation
| Clg | Clg-En | Clg-En Yes |  |  | No | [5 empty] | sets permission to allow UCB C1 and C2, ( 4-stage board C3 and C4) 24 VAC outputs for compressor contactor coils; Yes permits C1, C2 (C3 & C4) output, No does not permit C1, C2 (C3 & C4) output
|  | LeadLag-En | LeadLag-En No |  |  | Yes | [5 empty] | effective for 2 or more compressor stages; Yes permits compressor equalized runtime where the C# output with the least C#RunTim operates first, the the C# output with the next least C#RunTim operates second, etc. No operates the C1 output first, the C2 output second, etc.
|  | SATUp-Sp | SATUp-Sp 60 F |  |  | 41 F | through | 70 F |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units with occupied status; the cooling SAT setpoint in use when OpST falls below SATRst-Sp; must be set greater than SATLo-Sp
|  | SATLo-Sp | SATUp-Sp 60 F |  |  | 40 F | through | 63 F |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units with occupied status; the cooling SAT setpoint in use when OpST falls below SATRst-Sp; must be set less than SATUp-Sp
|  | SATRst-Sp | SATRst-Sp 72 F |  |  | 40 F | through | 85 F |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units with occupied status; SATUp-Sp in use when OpST falls below this setpoint, SATLo-Sp in use when OpST rises above this setpoint,
|  | VAVClgUnocc-Sp | VAVClgUnocc-Sp 85 F |  |  | 46 F | through | 99 F |  |  | FanCtl-Type = Variable Speed | no function
|  | ClgOcc-Sp | ClgOcc-Sp 72 F |  |  | 45 F | through | 98 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base cooling comfort temperature setpoint in use with occupied status; must be set equal to or less than ClgUnocc-Sp and equal to or greater than CVHtgOcc-SP
|  | ClgUnocc-Sp | ClgUnocc-Sp 80 F |  |  | 46 F | through | 99 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base cooling comfort temperature setpoint in use with unoccupied status; must be set equal to or greater than ClgOcc-Sp
|  | SZVAVClgOcc-Sp | SZVAVClgOcc-Sp 72 F |  |  | 45F | through | 98 F |  |  | SZVAVEn = On | effective for SZ VAV units with occupied status; the cooling space temperature setpoint in use
|  | SZVAVClgUnocc-Sp | SZVAVClgUnocc-Sp 85 F |  |  | 45F | through | 98 F |  |  | SZVAVEn = On | effective for SZ VAV units with unoccupied status; the cooling space temperature setpoint in use; OffDurUnocc must be set to No
| Htg | Htg-En | Htg-En Yes |  |  | No | [5 empty] | sets permission to allow UCB H1 and H2, ( 4-stage board H3) 24 VAC outputs for heat stages; Yes permits H1, H2 (& H3) output, No does not permit H1, H2 (& H3) output
|  | HtgOcc-En | HtgOcc-En No |  |  | Yes |  |  |  |  | FanCtl-Type ≠ Variable Speed | Yes sets permission to allow VAV unit heating operation with occupied status
|  | VAVHtgOcc-SP | VAVOcc-SP 68 F |  |  | 40 F | through | 85 F |  |  | FanCtl-Type ≠ Variable Speed | the heating space temperature setpoint in use for VAV units with occupied status and HtgOcc-En = Yes; requests for heating operation are initiated when OpST falls below this setpoint
|  | HtgUnocc-En | HtgUnocc-En No |  |  | Yes |  |  |  |  | FanCtl-Type ≠ Variable Speed | Yes sets permission to allow VAV unit heating operation with unoccupied status
|  | VAVHtgUnocc-Sp | VAVHtgUnocc-Sp 60 F |  |  | 45 F | through | 98 F |  |  | FanCtl-Type ≠ Variable Speed | the heating space temperature setpoint in use for VAV units with unoccupied status and HtgUnocc-En = Yes; requests for heating operation are initiated when OpST falls below this setpoint
|  | CVHtgOcc-SP | CVHtgOcc-SP 68 F |  |  | 46 F | through | 99 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base heating comfort temperature setpoint in use with occupied status; must be set equal to or less than ClgOcc-Sp and equal to or greater than CVHtgUnocc-Sp
|  | CVHtgUnocc-Sp | CVHtgUnocc-Sp 60 F |  |  | 45 F | through | 98 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base heating comfort temperature setpoint in use with unoccupied status; must be set equal to or less than CVHtgOcc-SP
|  | HydReverse | HydReverse No |  |  | Yes |  |  |  |  | Htg-Type - Proportional
|  | HydH1SA-Sp | HydH1SA-Sp 120 F | [7 empty] | Htg-Type - Proportional
|  | HydH2SA-Sp | HydH2SA-Sp 150 F | [7 empty] | Htg-Type - Proportional
|  | SATTempHydHt-En | SATTempHydHt-En No |  |  | Yes |  |  |  |  | Htg-Type - Proportional
|  | SATTempHydHt-Sp | SATTempHydHt-Sp 40 F | [7 empty] | Htg-Type - Proportional
| Econ | Econ-En | Econ-En Yes |  |  | No |  |  |  |  | economizer board | Yes sets permission to allow economizer free cooling operation, No does not permit economizer free cooling operation
|  | FreeClg-Sel | FreeClg-Sel Auto |  |  | Dry Bulb Temperature | Single Enthalpy | Dual Enthalpy |  |  | economizer board | sets the desired economizer free cooling changeover method; Auto sets the changever method based on the presence of economizer board OAH 2-10 VDC input and UCB RAH 2-10 VDC input, Dual Enthalpy requires OAH and RAH inputs to be effective, Single Enthalpy requires OAH input to be effective
|  | EconOAT-SpEn | EconOAT-SpEn 55 F |  |  | 40 F | through | 80 F |  |  | economizer board | dry bulb free cooling changeover setpoint; with FreeClg-Mode = Dry Bulb Tempe, economizer free cooling is available when OAT is below this setpoint
|  | EconOAEnth-Sp | EconOAEnth-Sp 27B/# |  |  | 10 B/# | through | 50 B/# |  |  | economizer board | single enthalpy free cooling changeover setpoint; with FreeClg-Mode = Single Enthalpy, economizer free cooling is available when OA-Enth is below this setpoint
|  | LowAmb-Sp | LowAmb-Sp 0 F |  |  | 0 F | through | 60 F |  |  | economizer board | with OprOAT below this setting LowAmb-MinPos is the effective economizer minimum position, with OprOAT below this setting Econ-MinPos is the effective economizer minimum position
|  | LowAmb-MinPos | LowAmb-MinPos 0% |  |  | 0% | through | 100% |  |  | economizer board | economizer minimum position effective with occupied status, indoor blower operation and when OAT is below LowAmb-Sp; typically set less than Econ-MinPos
|  | EconMechStp | EconMechStp Option B |  |  | Option A |  |  |  |  | economizer board | Option A - economizer damper position and/or time triggers compressor operation to supplement free cooling; Option B - supply air temperature with VAV supply air temperature (upper/lower) setpoint triggers compressor operation to supplement free cooling
|  | EconFltDetectEn | EconFltDetectEn Enable |  |  | Disable |  |  |  |  | economizer board | California Title 24 fault detection requirement
|  | EconAlrmDly | EconAlrmDly 600sec |  |  | 0sec | through | 3600sec |  |  | economizer board | California Title 24 fault detection requirement
|  | EconPosErr | EconPosErr 8% |  |  | 0% | through | 100% |  |  | economizer board | California Title 24 fault detection requirement
|  | EconMinErr | EconMinErr 5% |  |  | 0% | through | 100% |  |  | economizer board | California Title 24 fault detection requirement
| Dvent | Dvent-Mode | Dvent-Mode Disabled |  |  | Controlled by IAQ | Diff between IAQ and OAQ |  |  |  | economizer board | Demand Ventilation mode selection; Disabled permits no demand ventilation function, Controlled by IAQ requires IAQ input, Diff between IAQ and OAQ requires IAQ and OAQ inputs
|  | DVentMaxEconPos | DVentMaxEconPos 50% |  |  | 0% | through | 100% |  |  | economizer board | the maximum economizer actuator position for demand ventilation operation; termed "IAQEcon-MaxPos" elsewhere
|  | DVentIAQ-Sp | DVentIAQ-Sp 1000ppm |  |  | 0ppm | through | 5000ppm |  |  | economizer board | effective when DVent-Mode = Controlled by IAQ; with occupied status and indoor blower operation, demand ventilation operation the economizer is initiated if OprIAQ rises above this setpoint; adjustment increments of 1s
|  | DVentDiff-Sp | DVentDiff-Sp 600ppm |  |  | 0ppm | through | 5000ppm |  |  | economizer board | effective when DVent-Mode = Diff between IAQ and OAQ; with occupied status and indoor blower operation, demand ventilation operation the economizer is initiated if OprIAQ rises above OprOAQ plus this setpoint; adjustment increments of 1s
|  | IAQRange | IAQRange 2000ppm |  |  | 0ppm | through | 5000ppm |  |  | economizer board | setting only required when a CO₂ sensor is connected to the economizer board IAQ 0-10 VDC input; set for the CO₂ ppm measured at 10 VDC IAQ sensor output; adjustment increments of 1s
|  | OAQRange | OAQRange 2000ppm |  |  | 0ppm | through | 5000ppm |  |  | economizer board | setting only required when a CO₂ sensor is connected to the economizer board OAQ 0-10 VDC input; set for the CO₂ ppm measured at 10 VDC OAQ sensor output; adjustment increments of 1s
| PowerEx | Bldg-Sp | Bldg-Sp .100"/w |  |  | -249"/w | through | .249"/w |  |  | economizer board present and ExFType ≠ Non-Modulating | effective for Modulating Damper and Variable Frequency Fan power exhaust; building pressure setpoint for exhaust damer position/exhaust fan VFD speed control; 1/100th adjustment increments
|  | EconDmpPosFanOn | EconDmpPosFanOn 60 % |  |  | 20% | through | 99% |  |  | economizer board present and ExFType = Non-Modulating | effective for Non-Modulating power exhaust; the Econ position where the economizer board EX-FAN 24 VAC output is turned On; must be set greater than EconDmpPosFanOff
|  | EconDmpPosFanOff | EconDmpPosFanOff 20 % |  |  | 10% | through | 89% |  |  | economizer board present and ExFType = Non-Modulating | effective for Non-Modulating power exhaust; the Econ position where the economizer board EX-FAN 24 VAC output is turned Off; must be set greater than Econ-MinPos and less than EconDmpPosFanOff
|  | ExDmpPosFanOn | ExDmpPosFanOn 80 % |  |  | 20% | through | 99% |  |  | economizer board present and ExFType = Modulating Damper | effective for Modulating Damper power exhaust; the EAD-O position where the economizer board EX-FAN 24 VAC output is turned On; must be set greater than ExDmpPosFanOff
|  | ExDmpPosFanOff | ExDmpPosFanOff 20 % |  |  | 10% | through | 89% |  |  | economizer board present and ExFType = Modulating Damper | effective for Modulating Damper power exhaust; the EAD-O position where the economizer board EX-FAN 24 VAC output is turned Off; must be set less than ExDmpPosFanOn
|  | ERV-En | ERV-En No |  |  | Yes |  |  |  |  | economizer board | Yes sets economizer and power exhaust operation to integrate an exhaust recovery ventilator
| HGR | HGR-En | HGR-En No |  |  | Yes |  |  |  |  | HGR-En = On in Details>Service>Factory | Yes sets permission to allow hot gas reheat operation, No does not permit hot gas reheat operation
|  | HGRUnocc-En | HGRUnocc-En Yes |  |  | No |  |  |  |  | HGR-En = On | Yes sets permission to allow hot gas reheat operation when occupancy status is UnOccupied, No does not permit hot gas reheat operation when occupancy status is UnOccupied
|  | HGRAltWrite | HGRAltWrite Yes |  |  | No |  |  |  |  | HGR-En = On | Yes sets permission to allow access to hot gas reheat mode selection in HGRAlt-En; No does not permit access to hot gas reheat mode selection in HGRAlt-En
|  | HGRAlt-En | HGRAlt-En No |  |  | Yes |  |  |  |  | HGR-En = On | Yes sets either the Normal or Alternate hot gas reheat sequence
|  | HGRHum-Sp | HGRHum-Sp 60 %H |  |  | 0 | through | 100% |  |  | HGR-En = On | effective for hot gas reheat operation when Occupied; hot gas reheat operation is initiated when OprSH rises above this setpoint
|  | HGRUnoccHum-Sp | HGRUnoccHum-Sp 70 % |  |  | 0% | through | 100% |  |  | HGR-En = On | effective for hot gas reheat operation when UnOccupied; hot gas reheat operation is initiated when OprSH rises above this setpoint
| WarmupCooldown | OptStrt-En | OptStrt-En No |  |  | Yes |  |  |  |  | FanCtl-Type = Variable Speed
|  | EarlyStrtPeriod | EarlyStrtPeriod 60min |  |  | 0 | through | 120 min |  |  | FanCtl-Type = Variable Speed
|  | UseOccSched | UseOccSched Yes |  |  | No |  |  |  |  | FanCtl-Type = Variable Speed
| T24LoadShed | LoadShedRateLim | LoadShedRateLim .066 |  |  | 0 | through | 1 |  |  |  | California Title 24 function
|  | LoadShedAdjust | LoadShedAdjust 4.0 F |  |  | 0 | through | 8 |  |  |  | California Title 24 function
|  | LoadShedEnable | LoadShedActive No |  |  | Yes | [5 empty] | California Title 24 function
| Defrost | TestDefrostEnable | TestDefrostEnable No |  |  | Yes |  |  |  |  | #HtPumpStgs ≠ 0
|  | CompDelayEnable | CompDelayEnable No |  |  | Yes |  |  |  |  | #HtPumpStgs ≠ 0
|  | DefrostCurveSel | DefrostCurveSel Curve 1 |  |  | Curve 1 | through | Curve 6 |  |  | #HtPumpStgs ≠ 0 | See text
| Network | DevName | DevName UCBApp | [8 empty] | device name that appears on the FC BUS BACnet network
|  | BASCom | BASCom BACnet |  |  | Not Installed | [5 empty] | BACnet indicated with communication sub-board option
|  | Address | Address 4 |  |  | 0 | through | 127 |  |  |  | effective with communication sub-board option; FC BUS BACnet network address
| SZ VAV | DATClgMinSP | DATClgMinSP 54.0 F |  |  | 55.0 F | through | 60.0 F |  |  |  | effective with single zone VAV option; if SAT falls below this setpoint, fan speed is increased from SVVAVMinFan Spd
|  | DATMaxHtgSP | DATMaxHtgSP 105.0 F |  |  | 80.0 F | through | 110.0 F |  |  |  | effective with single zone VAV option; SAT setpoint for single zone VAV heating operation when the heating load % command is 75-100%
|  | DATSATSP | DATSATSP 70.0 F |  |  | 65.0 F | through | 75.0 F |  |  |  | effective with single zone VAV option; SAT setpoint for fan speed control in cooling operation when the cooling load command has remained at 100% for 5 minutes or more
|  | SZVAVMinFanSpd | SZVAVMinFanSpd 66% |  |  | 0% | through | 100% |  |  | SZVAVEn = On | effective with single zone VAV option; minimum fan speed for Fan Only and cooling operation
Controller | Firm | FirmVer | FirmVer 3.0.0.1059 | [8 empty] | UCB firmware revision
|  | Firm-S | FirmS Firmware Versions OK | [8 empty] | UCB firmware status
| Time | TimeZone | TimeZone Central |  |  | Mountain | Pacific | Newfoundland | Atlantic
[6 empty] | Alaska | Hawaii | Eastern
| Network | DevName | DevName UCBApp | [8 empty] | device name that appears on the FC BUS BACnet network
|  | BASCom | BASCom BACnet |  |  | Not Installed | [5 empty] | BACnet indicated with communication sub-board option
|  | Descrip | Descrip Smart Equipment 2 Stage
|  | Comm-S | Comm-S Active |  |  | Active | [5 empty] | effective when an optional communcation sub-board is present; Waiting For Pol indicates FC BUS network communication is not present, Active indicates FC BUS network communication is present
|  | FcBusMode | FcBusMode Wired Field Bus
|  | Address | Address 4 |  |  | 0 | through | 127 |  |  |  | effective with communication sub-board option; FC BUS BACnet network address
|  | OprBaudRate | OprBaudRate 38400 |  |  | 1200 | 9600 | 19200 |  |  |  | effective with communication sub-board option; FC BUS baud rate to be used
[6 empty] | 38400 | 76800
|  | BaudRate | BaudRate Auto |  |  | 1200 | 9600 | 19200 |  |  |  | effective with communication sub-board option; FC BUS baud rate in use
[6 empty] | 38400 | 76800
|  | DeviceId | DeviceId 1 |  |  | 0 | through | 4194302 |  |  |  | device ID number that appears on the FC BUS BACnet network; adjustment increments of 1s
| Misc | Language | Language English |  |  | French | Spanish |  |  |  |  | language used in the UCB parameter display
|  | Units | Units IP |  |  | SI | [5 empty] | IP uses Imperial units of measure in the UCB parameter display (°F, "wc, etc.), SI uses metric units of measure in the UCB parameter display (°C, kPA, etc.)
| SysCntlrs | Misc | Relearn | Relearn False |  | True | [5 empty] | a setting entry of True is a one-time clearing of the list of SA BUS devices in the UCB memory
|  |  | #NetSensors | #NetSensors 0 | [7 empty] | (not active for this software revision; the number of NetSensors currently in SA BUS communication with the UCB)
|  |  | EconCntlr | EconCntlr Not Present |  | Offline | Online |  |  |  |  | status of the economizer board SA BUS communication to the UCB; Not Present indicates SA BUS communication has not been established or relearned away, Online indicates SA BUS communication is established, Offline indicates SA BUS communication was once established and is currently lost
|  |  | 4StgCntlr | 4StgCntlr Not Present |  | Offline | Online |  |  |  |  | status of the 4-stage board SA BUS communication to the UCB; Not Present indicates SA BUS communication has not been established or relearned away, Online indicates SA BUS communication is established, Offline indicates SA BUS communication was once established and is currently lost
|  |  | FDDMCntlr | FDDMCntlr Not Present |  | Offline | Online |  |  |  |  | status of the refrigerant circuit #1 & #2 FDD board SA BUS communication to the UCB; Not Present indicates SA BUS communication has not been established or relearned away, Online indicates SA BUS communication is established, Offline indicates SA BUS communication was once established and is currently lost
|  |  | FDDSCntlr | FDDSCntlr Not Present |  | Offline | Online |  |  |  |  | status of the refrigerant circuit #3 & #4 FDD board SA BUS communication to the UCB; Not Present indicates SA BUS communication has not been established or relearned away, Online indicates SA BUS communication is established, Offline indicates SA BUS communication was once established and is currently lost
|  | UCB | UCBMainVer | UCBMainVer 3.0.0.1059 | [7 empty] | UCB firmware revision
|  |  | UCBAppVer | UCBAppVer 11.2.0.1009_2014.6.9.255 | [7 empty] | UCB software application revision
|  |  | UCBHardVer | UCBHardVer 0001 | [7 empty] | UCB hardware revision
|  | Econ | EconMainVer | EconMainVer 3.0.0.1059 | [6 empty] | economizer board present | economizer board firmware revision
|  |  | EconAppVer | EconAppVer 11.2.0.1009_2014.6.6.255 | [6 empty] | economizer board present | economizer board software application revision
|  |  | EconHardVer | EconHardVer 0001 | [6 empty] | economizer board present | economizer board hardware revision
|  | 4Stg | 4StgMainVer | 4StgMainVer 3.0.0.1070 | [6 empty] | 4-stage board present | 4-stage board firmware revision
|  |  | 4StgAppVer | 11.2.0.1017_2014.8.4.255 | [6 empty] | 4-stage board present | 4-stage board software application revision
|  |  | 4StgHardVer | 4StgHarVer | [6 empty] | 4-stage board present | 4-stage board hardware revision
|  | FDDMstr | FDDMMainVer | FDDMMainVer 3.0.0.1072 | [6 empty] | FDD board present | FDD board firmware revision
|  |  | FDDMAppVer | FDDMAppVer 11.2.0.1018 | [6 empty] | FDD board present | FDD board software application revision
|  |  | FDDMHardVer | FDDMHardVer 0001 | [6 empty] | FDD board present | FDD board hardware revision
|  | FDDS | FDDSMainVer | FDDSMainVer 3.0.0.1072 | [6 empty] | Second FDD board present | Second FDD board firmware revision
|  |  | FDDSAppVer | FDDSAppVer 11.2.0.1018 | [6 empty] | Second FDD board present | Second FDD board software application revision
|  |  | FDDSHardVer | FDDSHardVer | [6 empty] | Second FDD board present | Second FDD board hardware revision
Update | View Version | 3.0.0.1059 Firmware OK | [9 empty] | UCB firmware revision
| Load Firmware | No Package Present | [9 empty] | see text/image description of firmware update process via USB flash drive
| Backup | BKP:Wait | [9 empty] | see text/image description of backup process via USB flash drive
| Restore | serialflash/BackupConfig | [9 empty] | see text/image description of restore process via USB flash drive
| Full Clone | serialflash/BackupConfig | [9 empty] | see text/image description of full clone process via USB flash drive
| Partial Clone | serialflash/BackupConfig | [9 empty] | see text/image description of part clone process via USB flash drive
| Factory Defaults | Confirm | [9 empty] | a setting entry of Confirm restores the factory-built unit settings stored in the UCB memory
| Time | Hour 1 |  |  |  | 0 | through | 23 |  |  |  | Military (24 hour) time format
|  | Minute 1 |  |  |  | 0 | through | 59
|  | Day 11 |  |  |  | 1 | through | 31 |  |  |  | maximum Day depends on Month & Year selected
|  | Month 1 |  |  |  | 1 | through | 12
|  | Year 2000 |  |  |  | 1900 | through | 2155
Details | Unit | Unit-S | Unit-S Startup Delay
|  | Name | Name RTUxxxx | [8 empty] | 14 character maximum
|  | Model# | Model# RTUxxxxx | [8 empty] | 14 character maximum
|  | Serial# | Serial# DEFAULT_SERIAL | [8 empty] | 14 character maximum
|  | ModelName | ModelName SE-SPU1002-0 | [8 empty] | UCB part number
|  | ResetLO | ResetLO Off |  |  | On | [5 empty] | a setting entry of On resets active hard lockout alarms
|  | UnitEn | UnitEn Enable |  |  | Shutdown | [5 empty] | Enable allows unit operation, Shutdown does not allow unit operation; minimum run time delays apply
|  | HdwrReset | HdwrReset No |  |  | Yes
| Setpoints | OprST | OprST 70.1 F | [8 empty] | the buffered space temperature in use; may be from UCB RAT thermistor or ST thermistor input, SA BUS NetSensor or FC BUS communicated value sources
|  | OprOcc | OprOcc UnOccupied |  |  | Occupied | [5 empty] | occupancy status in use; the OccSrc parameter lists the source of occupied/unoccupied status; the OccMode parameter sets the occupied/unoccupied status initiation method
|  | RAT | RAT 70.1 F | [8 empty] | the buffered UCB RAT thermistor input
|  | DctPrs | DctPrs .97"/w | [7 empty] | FanCtl-Type ≠ Variable Speed | effective for VAV units; the buffered UCB DCT PRS 0-5 VDC input
|  | OprVAVClg-Sp | OprVAVClg-Sp 85 F |  |  | 85 F |  |  |  |  | FanCtl-Type ≠ Variable Speed | the VAV cooling SAT setpoint in use; with OprST above SATRst-Sp is SATLo-Sp, with OprST below SATRst-Sp is SATUp-Sp; cooling operation requests are initiated when OprST rises above this setpoint
|  | VAVOprHtg-Sp | VAVOprHtg-Sp 60 F |  |  | 60 F |  |  |  |  | FanCtl-Type ≠ Variable Speed | the VAV space heating setpoint in use; depending on occupied/unoccupied status and enabled VAV heating modes, is either MornWRAT-Sp or VAVHtgUnocc-Sp or VAVHtgOcc-SP; heating operation requests are initiated when OprST falls below this setpoint
|  | DctPrs-Sp | DctPrs-Sp 1.50"/w |  |  | .00"/w | through | 4.99"/w |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units; supply duct pressure setpoint for indoor blower speed control; 1/100th adjustment increments
|  | VAVClgUnocc-Sp | VAVClgUnocc-Sp 85 F | [7 empty] | FanCtl-Type ≠ Variable Speed | no function
|  | HtgOcc-En | HtgOcc-En Yes |  |  | No |  |  |  |  | FanCtl-Type ≠ Variable Speed | Yes sets permission to allow VAV unit heating operation with occupied status
|  | VAVHtgOcc-SP | VAVHtgOcc-SP 68 F |  |  | 40 F | through | 85 F |  |  | FanCtl-Type ≠ Variable Speed | the heating space temperature setpoint in use for VAV units with occupied status and HtgOcc-En = Yes; requests for heating operation are initiated when OpST falls below this setpoint
|  | HtgUnocc-En | HtgUnocc-En No |  |  | Yes |  |  |  |  | FanCtl-Type ≠ Variable Speed | Yes sets permission to allow VAV unit heating operation with unoccupied status
|  | VAVHtgUnocc-Sp | VAVHtgUnocc-Sp 60 F |  |  | 45 F | through | 98 F |  |  | FanCtl-Type ≠ Variable Speed | the heating space temperature setpoint in use for VAV units with unoccupied status and HtgUnocc-En = Yes; requests for heating operation are initiated when OpST falls below this setpoint
|  | OprCVClg-Sp | OprCVClg-Sp 85 F |  |  | 85 F |  |  |  |  | FanCtl-Type ≠ Variable Speed | effective if TSTstatTAT-Only = No; the CV cooling setpoint in use; depending on occupied/unoccupied status, is either ClgOcc-Sp ± OprSSO or ClgUnocc-Sp ± OprSSO; cooling operation requests are initiated when OprST rises above this setpoint
|  | CVOprHtg-Sp | CVOprHtg-Sp 60 F |  |  | 60 F | [5 empty] | effective if TSTstatTAT-Only = No; the CV heating setpoint in use; depending on occupied/unoccupied status, is either CVHtgOcc-Sp ± OprSSO or CVHtgUnocc-Sp ± OprSSO; heating operation requests are initiated when OprST falls below this setpoint
|  | ClgOcc-Sp | ClgOcc-Sp 72 F |  |  | 45 F | through | 98 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base cooling comfort temperature setpoint in use with occupied status; must be set equal to or less than ClgUnocc-Sp and equal to or greater than CVHtgOcc-SP
|  | ClgUnocc-Sp | ClgUnocc-Sp 80 F |  |  | 46 F | through | 99 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base cooling comfort temperature setpoint in use with unoccupied status; must be set equal to or greater than ClgOcc-Sp
|  | CVHtgOcc-SP | CVHtgOcc-SP 68 F |  |  | 46 F | through | 99 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base heating comfort temperature setpoint in use with occupied status; must be set equal to or less than ClgOcc-Sp and equal to or greater than CVHtgUnocc-Sp
|  | CVHtgUnocc-Sp | CVHtgUnocc-Sp 60 F |  |  | 45 F | through | 98 F |  |  | FanCtl-Type ≠ Variable Speed | effective for CV units if TSTstatTAT-Only = No; the base heating comfort temperature setpoint in use with unoccupied status; must be set equal to or less than CVHtgOcc-SP
|  | SAT | SAT 60.6 F | [8 empty] | the buffered UCB SAT thermistor input
|  | SATUp-Sp | SATUp-Sp 60 F |  |  | 41 F | through | 70 F |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units with occupied status; the cooling SAT setpoint in use when OpST falls below SATRst-Sp; must be set greater than SATLo-Sp
|  | SATLo-Sp | SATLo-Sp 55 F |  |  | 40 F | through | 69 F |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units with occupied status; the cooling SAT setpoint in use when OpST falls below SATRst-Sp; must be set less than SATUp-Sp
|  | SATRst-Sp | SATRst-Sp 72 F |  |  | 40 F | through | 85 F |  |  | FanCtl-Type ≠ Variable Speed | effective for VAV units with occupied status; SATUp-Sp in use when OpST falls below this setpoint, SATLo-Sp in use when OpST rises above this setpoint,
| Zone | Indoor | OprST | OprST 75.7 F | [7 empty] | the buffered space temperature in use; may be from UCB RAT thermistor or ST thermistor input, SA BUS NetSensor or FC BUS communicated value sources
|  |  | OprOcc | OprOcc UnOccupied |  | Occupied | [5 empty] | occupancy status in use; the OccSrc parameter lists the source of occupied/unoccupied status; the OccMode parameter sets the occupied/unoccupied status initiation method
|  |  | OprIAQ | OprIAQ 473ppm |  | Input Unreliable |  |  |  |  | economizer board present | the buffered indoor air quality in use; may be from economizer board IAQ 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates IAQ input is currently not present
|  |  | OprSH | OprSH 19.6 %H |  | Input Unreliable |  |  |  |  | input to the UCB RAH pins, humidity from NetSensor or communicated value | the buffered space humidity in use; may be from UCB RAH 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates RAH input was once detected and is currently lost
|  |  | OprFanReq | OprFanReq On |  | Off | [5 empty] | indoor blower operation request status; source of request may be 24 VAC input to the UCB G terminal, heating operation, cooling operation, occupied status, heating limit trip, purge input or FC BUS communicated command
|  |  | OprSSO | OprSSO 3.0 F |  | Input Unreliable |  |  |  |  | input to the UCB SSO terminal, SSO from NetSensor or communicated value | the buffered space setpoint offset in use; may be from UCB SSO 0-20,000 Ω input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates SSO input was once detected and is currently lost
|  |  | SSO | SSO .0 F |  | Input Unreliable |  |  |  |  | input to the UCB SSO terminal | the buffered UCB SSO 0-20,000 Ω input
|  |  | SSORange | SSORange 3.0 F |  | .0 F | through | 5.0 F |  |  |  | the maximum above/below alteration permitted for space setpoint offset to adjust CV comfort setpoints; 1/10th adjustment increments
|  |  | STSrc | STSrc Network Sensor |  | Local Input | Network Sensor | BAS Override |  |  |  | the source of the space temperature input in use; Return Air Tem is from UCB RAT thermistor input, Local is from UCB ST thermistor input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value
|  |  | STAlarmOffset | STAlarmOffset 5 F |  | 0 F | through | 25 F |  |  |  | effective for CV units; the temperature amount above OprCVClg-Sp or below CVOprHtg-Sp for Opr ST to begin the STAlarmDelay timer
|  |  | STAlarmDelay | STAlarmDelay 60min |  | 0min | through | 120min |  |  |  | effective for CV units; the continuous time with STAlarmOffset exceeded to generate space temperature alarm notification
|  |  | OccSrc | OccSrc Local Input |  | BAS Network Req | [5 empty] | the source of occupied/unoccupied status; Local Input is 24 VAC input to the UCB OCC terminal, (Schedule is from the UCB schedule), BAS Network Req is from FC BUS communicated value
|  |  | TempOccTimeout | TempOccTimeout 120min |  | 30min | through | 480min |  |  |  | the maximum time from initiation for temporary occupancy to be in effect; temporary occupancy may be initiated from UCB ST thermistor input (momentarily shorted), SA BUS NetSensor or FC BUS communicated value sources
|  |  | OccMode | OccMode External |  | Schedule | [5 empty] | sets occupied/unoccupied status initiation method; External permits occupied/unoccupied status initiation by 24 VAC input to the UCB OCC terminal or by FC BUS communicated value, (not to be used until schedule access provisions are made in later control revisions, Schedule permits occupied/unoccupied status initiation by the schedule held in the UCB)
|  |  | IAQSrc | IAQSrc Local Input |  | Input Unreliable | BAS Override |  |  |  | economizer board present | the source of the indoor air quality input in use; Local is from the economizer board IAQ 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates IAQ input is currently not present
|  |  | SHSrc | SHSrc Local Input |  | Input Unreliable | BAS Override |  |  |  |  | the source of the space humidity input in use; Local is from UCB RAH 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates SH input is currently not present
|  |  | FanReqSrc | FanReqSrc Local Input |  | BAS Override | [5 empty] | the source of the indoor blower operation request in use; Local is from 24 VAC input to the UCB G terminal, heating operation, cooling operation, occupied status, heating limit trip or purge input; BAS Override is from FC BUS communicated command
|  |  | SSOSrc | SSOSrc Network Sensor |  | Input Unreliable | Network Sensor | BAS Override |  |  |  | the source of the space setpoint offset in use; Local is from UCB SSO 0-20,000 Ω input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates SSO input is currently not present
|  |  | OffDurUnocc | OffDurUnocc No |  | Yes | [5 empty] | Unit operation not permitted during UnOccupied mode
|  |  | UseOccSched | UseOccSched Yes |  | No
|  | Outdoor | OprOAT | OprOAT 70.0 F | [7 empty] | the buffered outdoor air temperature in use; may be from UCB OAT thermistor input or FC BUS communicated value sources
|  |  | OprOAH | OprOAH 19 %H |  | Input Unreliable |  |  |  |  | economizer board present | the buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; ?Unrel indicates OAH input is currently not present
|  |  | OA-Enth | OA-Enth 0B/# |  | 0 B/# | [5 empty] | enthalpy calculated from OAH 0-10 VDC input to the economizer board and OprOAT; 0B/# indicated if OAH 0-10 VDC input to the economizer board is not present
|  |  | OprOAQ | OprOAQ 195ppm |  | Input Unreliable |  |  |  |  | economizer board present | the buffered outdoor air quality in use; may be from economizer board OAQ 0-10 VDC input or FC BUS communicated value sources; ?Unrel indicates OAQ input is currently not present
|  |  | OATSrc | OATSrc Local Input |  | BAS Override | [5 empty] | the source of the outdoor air temperature input in use; Local is from UCB OAT thermistor input, BAS Override is from FC BUS communicated value
|  |  | OAHSrc | OAHSrc Local Input |  | Input Unreliable | BAS Override |  |  |  | economizer board present | the source of the outdoor air humidity input in use; Local is from economizer board OAH 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
|  |  | OAQSrc | OAQSrc Local Input |  | Input Unreliable | BAS Override |  |  |  | economizer board present | the source of the outdoor air quality input in use; Local is from economizer board OAQ 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
| Control | IndoorFan | Status | Fan | Fan Off | On | [5 empty] | UCB FAN 24 VAC output status
|  |  |  | FanVFD | FanVFD 0 % | [5 empty] | FanCtl-Type ≠ Single Speed | UCB VFD 2-10 VDC output status
|  |  |  | FanCtl-Type | FanCtl-Type Single Speed | Two Speed | Fixed Variable | Variable Speed |  |  |  | indoor blower and unit operating mode selection; Single Speed = CV unit w/o indoor blower VFD, (Two Speed = CV unit w/2-step indoor blower VFD speed control), Fixed Variable = CV unit w/IntelliSpeed indoor blower VFD speed control, Variable Speed = VAV unit w/supply duct static/indoor blower VFD speed control
|  |  |  | APS | APS Off | On | [5 empty] | UCB APS 24 VAC input status; Off indicates 0 VAC input to the APS pin, On indicates 24 VAC input to the APS pin
|  |  |  | DctPrs | DctPrs .96"/w | [5 empty] | FanCtl-Type = Variable Speed | effective for VAV units; the buffered UCB DCT PRS 0-5 VDC input
|  |  |  | SAT | SAT 60.6 F | [6 empty] | the buffered UCB SAT thermistor input
|  |  |  | FanOvrload | FanOvrload Normal | Alarm | [5 empty] | UCB FAN OVR 24 VAC input status; Normal indicates 24 VAC input to the FAN OVR pin, Alarm indicates 0 VAC input to the FAN OVR pin
|  |  |  | FanVFDFlt | FanVFDFlt Normal | Alarm |  |  |  |  | FanCtl-Type ≠ Single Speed | UCB VFD FLT 24 VAC input status; Normal indicates 0 VAC input to the VFD FLT pin, Alarm indicates 24 VAC input to the VFD FLT pin
|  |  |  | Fan-RT | Fan-RT .0 hr | .0 hr | through | ?????? |  |  |  | accumulated run time of UCB FAN 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | DFS | DFS Normal | Alarm | [5 empty] | UCB DFS 24 VAC input status; Normal indicates 0 VAC input to the DFS pin, Alarm indicates 24 VAC input to the DFS pin
|  |  | Setup | LowAmbFanPrerun | LowAmbFanPrerun 60sec | 0 sec | through | 255 sec |  |  |  | the amount of time the indoor blower must operate before compressor operation is permitted when OprOAT is below LowAmb10On5OffSp
|  |  |  | FanOnDlyCool | FanOnDlyCool 0sec | 0sec | through | 30sec |  |  |  | the amount of time indoor blower operation is delayed following the initiation of cooling operation
|  |  |  | FanOffDlyCool | FanOffDlyCool 30sec | 0sec | through | 255sec |  |  |  | the amount of time indoor blower operation is maintained following the termination of cooling operation
|  |  |  | FanOnDlyHeat | FanOnDlyHeat 30sec | 0sec | through | 30sec |  |  | #HtgStgs = 1 or more | the amount of time indoor blower operation is delayed following 24 VAC input to the UCB MV pin being received; must be set to 0 for unit with electric heat
|  |  |  | FanOffDlyHeat | FanOffDlyHeat 60sec | 0sec | through | 255sec |  |  | #HtgStgs = 1 or more | the amount of time indoor blower operation is maitained following 24 VAC input to the UCB MV pin being lost
|  |  |  | DctPrs-Sp | DctPrs-Sp 1.50"/w | .00"/w | through | 4.99"/w |  |  | FanCtl-Type = Variable Speed | effective for VAV units; supply duct pressure setpoint for indoor blower speed control; 1/100th adjustment increments
|  |  |  | DctShutdownSp | DctShutdownSp 4.50"/w | .01"/w | through | 4.99"/w |  |  | FanCtl-Type = Variable Speed | effective for VAV units; supply duct pressure unit shutdown setpoint; indoor blower and unit operation terminated if DctPrs rises above this setpoint: 1/100th adjustment increments
|  |  |  | FanOnOcc | FanOnOcc Yes | No |  |  |  |  | FanCtl-Type = Variable Speed | effective for CV units; Yes = UCB FAN output is on during occupied status, cycles with heating/cooling operation and fan request during unoccupied status; No = UCB FAN output cycles with heating/cooling operation and fan request
|  |  |  | FanOffStartHeat | FanOffStartHeat No | No |  |  |  |  | FanCtl-Type = Variable Speed | Yes interrupts an existing indoor blower operation request from the initiation of a 1st stage heating operation request until the UCB receives 24 VAC input to the MV pin and the FanOnDlyHeat expires, No does not interrupt an existing indoor blower operation request at the initiation of heating operation
|  |  |  | Fan Only-%Cmd | Fan Only-%Cmd 50% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during indoor blower-only operation
|  |  |  | 1ClgStg-%Cmd | 1ClgStg-%Cmd 70% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 1-stage cooling operation
|  |  |  | 2ClgStg-% Cmd | 2ClgStg-% Cmd 80% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 2-stage cooling operation
|  |  |  | 3ClgStg-% Cmd | 3ClgStg-% Cmd 90% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 3-stage cooling operation
|  |  |  | 4ClgStg-% Cmd | 4ClgStg-% Cmd 100% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 4-stage cooling operation
|  |  |  | 1HtgStg-% Cmd | 1HtgStg-% Cmd 100% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 1-stage heating operation
|  |  |  | 2HtgStg-% Cmd | 2HtgStg-% Cmd 100% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 2-stage heating operation
|  |  |  | 3HtgStg-% Cmd | 3HtgStg-% Cmd 100% | 0% | through | 100% |  |  | FanCtl-Type = Fixed Variable | effective for CV units with IntelliSpeed indoor blower VFD speed control; the UCB VFD 2-10 VDC output during 3-stage heating operation
|  | Clg | Status | Clg-S | Clg-S Off-Idle
|  |  |  | #ClgStgs | #ClgStgs 2 | 1 | through | 4 |  |  |  | number of compressor cooling stages; 1 or more enables the UCB C1 24 VAC output, 2 or more enables the UCB C2 24 VAC output, (3 or more enables the 4-stage board C3 24 VAC output, 4 enables the 4-stage board C4 24 VAC output)
|  |  |  | SAT | SAT 60.6 F | [6 empty] | the buffered UCB SAT thermistor input
|  |  |  | StgClgCmd | StgClgCmd 0% | 0% | through | 100% |  |  |  | With comfort control by sensors, contributes to the staging of the compressors
|  |  | Stage 1 | C1-S | C1-S Off-Idle
|  |  |  | C1-S | C1 Off | On
|  |  |  | C1-En | C1-En Yes | No | [5 empty] | Yes permits UCB C1 24 VAC output; independent of #ClgStgs selection, No does not permit UCB C1 24 VAC output
|  |  |  | C1OnTmr | C1OnTmr 0sec | [6 empty] | active number of minutes remaining for C1 minimum run timer expiration
|  |  |  | C1ASCDTmr | C1ASCDTmr 0sec | [6 empty] | active number of minutes remaining for C1 anti-short cycle delay timer expiration
|  |  |  | C1RunTim | C1RunTim .0 hr | 0 | through | ????? |  |  |  | accumulated run time of UCB C1 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EC1 | EC1 42.4 F | [6 empty] | the buffered UCB EC1 thermistor input
|  |  |  | CC1 | CC-1 96 F | [5 empty] | input to the UCB CC1 pins | the buffered UCB CC1 thermistor input
|  |  |  | SLP-1 | SLP-1 371.1psi | [5 empty] | FDD board present | the buffered FDD master SLP1 pressure transducer input
|  |  |  | LLP-1 | LLP-1 371.6psi | [5 empty] | FDD board present | the buffered FDD master LLP1 pressure transducer input
|  |  |  | SLT-1 | SLT-1 123.9 F | [5 empty] | FDD board present | the buffered FDD master SLT1 thermistor input
|  |  |  | LLT-1 | LLT-1 74.2 F | [5 empty] | FDD board present | the buffered FDD master LLT1 thermistor input
|  |  |  | C1-EI | C1-EI ? F | [5 empty] | FDD board present
|  |  |  | C1-CI | C1-CI ? F | [5 empty] | FDD board present
|  |  |  | C1-CondTempOvrAmb | C1-CondTempOvrAmb ? F | [5 empty] | FDD board present
|  |  |  | C1-EvapTempValue | C1-EvapTempValue ? F | [5 empty] | FDD board present
|  |  | Stage 2 | C2-S | C2-S Off-Idle | [5 empty] | #ClgStgs = 2 or more
|  |  |  | C2 | C2 Off | On |  |  |  |  | #ClgStgs = 2 or more | effective for units with 2 or more compressor cooling stages; UCB C2 24 VAC output status
|  |  |  | C2-En | C2-En Yes | No |  |  |  |  | #ClgStgs = 2 or more | Yes permits UCB C2 24 VAC output; independent of #ClgStgs selection, No does not permit UCB C1 24 VAC output
|  |  |  | C2OnTmr | C2OnTmr 0sec | [5 empty] | #ClgStgs = 2 or more | active number of minutes remaining for C2 minimum run timer expiration
|  |  |  | C2ASCDTmr | C2ASCDTmr 0sec | [5 empty] | #ClgStgs = 2 or more | active number of minutes remaining for C2 anti-short cycle delay timer expiration
|  |  |  | C2RunTim | C2RunTim 0 hr | .0 hr | through | ????? |  |  | #ClgStgs = 2 or more | accumulated run time of UCB C2 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EC2 | EC2 132.0 F | [5 empty] | #ClgStgs = 2 or more | the buffered UCB EC2 thermistor input
|  |  |  | CC2 | CC-2 96 F | [5 empty] | input to the UCB CC2 pins | the buffered UCB CC2 thermistor input
|  |  |  | SLP-2 | SLP-2 372.5psi | [5 empty] | FDD board present | the buffered FDD master SLP2 pressure transducer input
|  |  |  | LLP-2 | LLP-2 372.4psi | [5 empty] | FDD board present | the buffered FDD master LLP2 pressure transducer input
|  |  |  | SLT-2 | SLT-2 130.9 F | [5 empty] | FDD board present | the buffered FDD master SLT2 thermistor input
|  |  |  | LLT-2 | LLT-2 69.8 F | [5 empty] | FDD board present | the buffered FDD master LLT2 thermistor input
|  |  |  | C2-EI | C2-EI ? F | [5 empty] | FDD board present
|  |  |  | C2-CI | C2-CI ? F | [5 empty] | FDD board present
|  |  |  | C2-CondTempOvrAmb | C2-CondTempOvrAmb ? F | [5 empty] | FDD board present
|  |  |  | C2-EvapTempValue | C2-EvapTempValue ? F | [5 empty] | FDD board present
|  |  | Stage 3 | C3-S | C3-S Off-Idle
|  |  |  | C3 | C3 Off | On |  |  |  |  | #ClgStgs = 3 or more | effective for units with 3 or more compressor cooling stages; UCB C3 24 VAC output status
|  |  |  | C3-En | C3-En Yes | No |  |  |  |  | #ClgStgs = 3 or more | Yes permits UCB C3 24 VAC output; independent of #ClgStgs selection, No does not permit UCB C3 24 VAC output
|  |  |  | C3OnTmr | C3OnTmr 0sec | [5 empty] | #ClgStgs = 3 or more | active number of minutes remaining for C3 minimum run timer expiration
|  |  |  | C3ASCDTmr | C3ASCDTmr 0sec | [5 empty] | #ClgStgs = 3 or more | active number of minutes remaining for C3 anti-short cycle delay timer expiration
|  |  |  | C3RunTim | C3RunTim 0 hr | .0 hr | through | ????? |  |  | #ClgStgs = 3 or more | accumulated run time of UCB C3 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EC3 | EC3 96.6 F | [5 empty] | #ClgStgs = 3 or more | the buffered UCB EC3 thermistor input
|  |  |  | CC3 | CC-3 96 F | [5 empty] | input to the 4-stage board CC3 pins | the buffered 4-stage board CC3 thermistor input
|  |  |  | SLP-3 | SLP-3 372.5psi | [5 empty] | Second FDD board present | the buffered FDD slave SLP3 pressure transducer input
|  |  |  | LLP-3 | LLP-3 372.4psi | [5 empty] | Second FDD board present | the buffered FDD slave LLP3 pressure transducer input
|  |  |  | SLT-3 | SLT-3 130.9 F | [5 empty] | Second FDD board present | the buffered FDD slave SLT3 thermistor input
|  |  |  | LLT-3 | LLT-3 69.8 F | [5 empty] | Second FDD board present | the buffered FDD slave LLT3 thermistor input
|  |  |  | C3-EI | C3-EI ? F | [5 empty] | Second FDD board present
|  |  |  | C3-CI | C3-CI ? F | [5 empty] | Second FDD board present
|  |  |  | C3-CondTempOvrAmb | C3-CondTempOvrAmb ? F | [5 empty] | Second FDD board present
|  |  |  | C3-EvapTempValue | C3-EvapTempValue ? F | [5 empty] | Second FDD board present
|  |  | Stage 4 | C4-S | C4-S Off-Idle
|  |  |  | C4 | C4 Off | On |  |  |  |  | #ClgStgs = 4 or more | effective for units with 4 or more compressor cooling stages; UCB C4 24 VAC output status
|  |  |  | C4-En | C4-En Yes | No |  |  |  |  | #ClgStgs = 4 or more | Yes permits UCB C4 24 VAC output; independent of #ClgStgs selection, No does not permit UCB C4 24 VAC output
|  |  |  | C4OnTmr | C4OnTmr 0sec | [5 empty] | #ClgStgs = 4 or more | active number of minutes remaining for C4 minimum run timer expiration
|  |  |  | C4ASCDTmr | C4ASCDTmr 0sec | [5 empty] | #ClgStgs = 4 or more | active number of minutes remaining for C4 anti-short cycle delay timer expiration
|  |  |  | C4RunTim | C4RunTim 0 hr | 0 | through | ????? |  |  | #ClgStgs = 4 or more | accumulated run time of UCB C4 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EC4 | EC4 127.8 F | [5 empty] | #ClgStgs = 4 or more | the buffered UCB EC4 thermistor input
|  |  |  | CC4 | CC4 96 F | [5 empty] | input to the 4-stage board CC4 pins | the buffered 4-stage board CC4 thermistor input
|  |  |  | SLP-4 | SLP-4 372.5psi | [5 empty] | Second FDD board present | the buffered FDD slave SLP4 pressure transducer input
|  |  |  | LLP-4 | LLP-4 372.4psi | [5 empty] | Second FDD board present | the buffered FDD slave LLP4 pressure transducer input
|  |  |  | SLT-4 | SLT-4 130.9 F | [5 empty] | Second FDD board present | the buffered FDD slave SLT4 thermistor input
|  |  |  | LLT-4 | LLT-4 69.8 F | [5 empty] | Second FDD board present | the buffered FDD slave LLT4 thermistor input
|  |  |  | C4-EI | C4-EI ? F | [5 empty] | Second FDD board present
|  |  |  | C4-CI | C4-CI ? F | [5 empty] | Second FDD board present
|  |  |  | C4-CondTempOvrAmb | C4-CondTempOvrAmb ? F | [5 empty] | Second FDD board present
|  |  |  | C4-EvapTempValue | C4-EvapTempValue ? F | [5 empty] | Second FDD board present
|  |  | Setup | Clg-En | Clg-En Yes | No | [5 empty] | sets permission to allow UCB C1 and C2, ( 4-stage board C3 and C4) 24 VAC outputs for compressor contactor coils; Yes permits C1, C2 (C3 & C4) output, No does not permit C1, C2 (C3 & C4) output
|  |  |  | MinRtCoolStg | MinRtCoolStg 3min | 3min | through | 10min |  |  |  | sets the minimum run time for C# outputs; individual C# minimum run time begins when the output is turned on ; unless interrupted by safety shutdown, output is mantained until the individual C# minimum run time expires
|  |  |  | LeadLag-En | LeadLag-En No | Yes | [5 empty] | effective for 2 or more compressor stages; Yes permits compressor equalized runtime where the C# output with the least C#RunTim operates first, the the C# output with the next least C#RunTim operates second, etc. No operates the C1 output first, the C2 output second, etc.
|  |  |  | LowAmbFanPrerun | LowAmbFanPrerun 60sec | 0 sec | through | 255 sec |  |  |  | the amount of time the indoor blower must operate before compressor operation is permitted when OprOAT is below LowAmb10On5OffSp
|  |  |  | ClgOATCutout-En | ClgOATCutout-En Yes | No | [5 empty] | Yes does not permit C# output if OprOAT falls below ClgOATCutout, No permits C# output at any OprOAT
|  |  |  | ClgOATCutout | ClgOATCutout 45 F | 0 F | through | 100 F |  |  |  | if ClgOATCutout-En = Yes, C# output is not permitted if OprOAT falls below this setpoint
|  |  |  | ClgAdapTunEn | ClgAdapTunEn Yes | No
|  |  |  | SATCoolLimit-En | SATCoolLimit-En Yes | No | [5 empty] | Yes does not permit C# output if SAT falls below SATCoolLimit-Sp, No permits C# output at any SAT
|  |  |  | SATCoolLimit-Sp | SATCoolLimit-Sp 50 F | 40 F | through | 65 F |  |  |  | if SATCoolLimit-En = Yes, C# output is not permitted if SAT falls below this setpoint
|  |  |  | EconLoad-En | EconLoad-En No | Yes | [5 empty] | No does not permit economizer loading; effective if SATCoolLimit-En = Yes and OAT is above 60°F, Yes permits increased Econ position when all but one C# output has been cutoff due to SAT below SATCoolLimit-Sp
|  |  |  | AllCompOff-Econ | AllCompOff-Econ No | Yes |  |  |  |  | economizer board present | Yes does not permit compressor operation during free cooling; No permits compressor operation during free cooling
|  |  |  | LowAmb-En | LowAmb-En No | Yes | [5 empty] | Yes permits compressor operation to 0 F without 10 minute on and 5 minute off cycling
|  |  |  | LowAmb10On5OffSp | LowAmb10On5OffSp 45 F | 0 F | through | 60 F |  |  |  | if compressor operation otherwise is permitted, C# output cycled on 10 minutes/off 5 minutes with OprOAT below this setpoint
|  |  |  | TempHumCtrl-En | TempHumCtrl-En No | Yes | [5 empty] | No does not permit OprSH above TempHum-Sp to decrease OprCVClg-Sp, Yes permits OprSH above TempHum-Sp to decrease OprCVClg-Sp up to the amount set for MaxTempHumSpOff
|  |  |  | TempHum-Sp | TempHum-Sp 50 %H | 20 %H | through | 80 %H |  |  | TempHumCtrl = Yes | effective if TempHumCtrl-En = Yes; OprSH above this setpoint decreases OprCVClg-Sp up to the amount set for MaxTempHumSpOff
|  |  |  | MaxTempHumSpOff | MaxTempHumSpOff 3.0 F | .0 F | through | 5.0 F |  |  | TempHumCtrl = Yes | effective if TempHumCtrl-En = Yes; maximimum amount OprSH above TempHum-Sp decreases OprCVClg-Sp; 1/10th adjustment increments
|  |  |  | TempHumValPerDegOff | TempHumValPerDegOff 5 %H | 1 %H | through | 10 %H |  |  | TempHumCtrl = Yes | effective if TempHumCtrl-En = Yes; sets humidity increments of OprSH above TempHum-Sp to decrease OprCVClg-Sp by 1°F, up to the amount set for MaxTempHumSpOff; adjustment increments of 1s
|  |  |  | MornC-En | MornC-En No | Yes |  |  |  |  | SZVAVEn = On
|  |  |  | MornCRAT-Sp | MornCRAT-Sp 74 F | 50 F | through | 85 F |  |  | SZVAVEn = On
|  | Htg | Status | Htg-S | Htg-S Off-Disabled
|  |  |  | Htg-Type | Htg-Type Staged | Proportional | [5 empty] | sets heating control method; Staged permits UCB H1, H2 (& 4-stage board H3) 24 VAC outputs, (not to be used until provivions are made in later control revisions, Proportional permits 4-stage board MOD HT 2-10 VDC output)
|  |  |  | #HtgStgs | #HtgStgs 1 | 0 | through | 3 |  |  | Htg-Type = Staged | number of heating stages; 1 or more enables the UCB H1 24 VAC output, 2 or more enables the UCB H2 24 VAC output, (3 enables the 4-stage board H3 24 VAC output)
|  |  |  | HWV | HWV 0 % | [5 empty] | 4-stage board present | 4-stage board 2-10 VDC output status
|  |  |  | StgHtgCmd | StgHtgCmd 0% | 0% | through | 100% |  |  |  | With comfort control by sensors, contributes to staging during heating operation
|  |  | Stage 1 | H1-S | H1-S Off-Idle
|  |  |  | H1 | H1 Off | On |  |  |  |  | #HtgStgs = 1 or more | effective for units with 1 or more heating stages; UCB H1 24 VAC output status
|  |  |  | H1OnTmr | H1OnTmr 0sec | [5 empty] | #HtgStgs = 1 or more | active number of minutes remaining for H1 minimum run timer expiration
|  |  |  | H1ASCDTmr | H1ASCDTmr 0sec | [5 empty] | #HtgStgs = 1 or more | active number of minutes remaining for H1 anti-short cycle delay timer expiration
|  |  |  | H1RunTim | H1RunTim .0 hr | .0 hr | through | ????? |  |  | #HtgStgs = 1 or more | accumulated run time of UCB H1 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  | Stage 2 | H2-S | H2-S Off-Idle
|  |  |  | H2 | H2 Off | On |  |  |  |  | #HtgStgs = 2 or more | effective for units with 2 or more heating stages; UCB H2 24 VAC output status
|  |  |  | H2OnTmr | H2OnTmr 0sec | [5 empty] | #HtgStgs = 2 or more | active number of minutes remaining for H2 minimum run timer expiration
|  |  |  | H2ASCDTmr | H2ASCDTmr 0sec | [5 empty] | #HtgStgs = 2 or more | active number of minutes remaining for H2 anti-short cycle delay timer expiration
|  |  |  | H2RunTim | H2RunTim .0 hr | .0 hr | through | ????? |  |  | #HtgStgs = 2 or more | accumulated run time of UCB H2 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  | Stage 3 | H3-S | H3-S Off-Idle
|  |  |  | H3 | H3 Off | On |  |  |  |  | #HtgStgs = 3 or more | effective for units with 3 or more heating stages; UCB H3 24 VAC output status
|  |  |  | H3OnTmr | H3OnTmr 0sec | [5 empty] | #HtgStgs = 3 or more | active number of minutes remaining for H3 minimum run timer expiration
|  |  |  | H3ASCDTmr | H3ASCDTmr 0sec | [5 empty] | #HtgStgs = 3 or more | active number of minutes remaining for H3 anti-short cycle delay timer expiration
|  |  |  | H3RunTim | H3RunTim 0 hr | .0 hr | through | ????? |  |  | #HtgStgs = 3 or more | accumulated run time of UCB H3 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  | Setup | Htg-En | Htg-En Yes | No | [5 empty] | sets permission to allow UCB H1 and H2, ( 4-stage board H3) 24 VAC outputs for heat stages; Yes permits H1, H2 (& H3) output, No does not permit H1, H2 (& H3) output
|  |  |  | SATHtgLimit-En | SATHtgLimit-En Yes | No | [5 empty] | Yes does not permit H# output if SAT rises above SATHtgLimit-Sp, No permits H# output at any SAT
|  |  |  | SATHtgLimit-Sp | SATHtgLimit-Sp 135 F | 100 F | through | 180 F |  |  |  | if SATHtgLimit-En = Yes H# output is not permitted if SAT rises above this setpoint
|  |  |  | HtgOATCutout-Sp | HtgOATCutout-Sp 75 F | 0 F | through | 100 F |  |  |  | H# output (and hydronic heat operation) is not permitted if OprOAT rises above this setpoint
|  |  |  | HtgAdapTunEn | HtgAdapTunEn Yes | No | [5 empty] | On enables the heating cycle rate algorithm ; Off does not enable the heating cycle rate algorithm
|  |  |  | HydH1SA-Sp | HydH1SA-Sp 120 F | 80 F | through | 180 F |  |  | Htg-Type = Proportional | SAT setpoint for hydronic heat operation with a 1st stage heating request
|  |  |  | HydH2SA-Sp | HydH2SA-Sp 150 F | 80 F | through | 180 F |  |  | Htg-Type = Proportional | SAT setpoint for hydronic heat operation with a 2nd stage heating request
|  |  |  | SATTempHydHt-En | SATTempHydHt-En No | Yes |  |  |  |  | Htg-Type = Proportional | (not to be used until provivions are made in later control revisions, Yes permits hydronic heat supply air tempering)
|  |  |  | HydReverse | HydReverse No | Yes |  |  |  |  | Htg-Type = Proportional | sets action of 4-stage board MOD HT 2-10 VDC output; No sets MOD HT output at 2 VDC is 0%/closed and at 10 VDC is 100%/open, Yes sets MOD HT output at 10 VDC is 0%/closed and at 2 VDC is 100%/open
|  |  |  | MornW-En | MornW-En No | Yes |  |  |  |  | FanCtl-Type = Variable Speed | Yes permits VAV unit heating operation for morning warm up
|  |  |  | MornWRAT-Sp | MornWRAT-Sp 71 F | 50 F | through | 85 F |  |  | FanCtl-Type = Variable Speed | If MornW-En = Yes, VAV unit heating will operate during morning warm up until RAT reaches this setpoint
|  | Heat Pump | Status | Clg-S | Clg-S
|  |  |  | Htg-S | Htg-S
|  |  |  | C1 | C1 Off | On | [5 empty] | UCB C1 24 VAC output status
|  |  |  | C2 | C2 | On | [5 empty] | UCB C2 24 VAC output status
|  |  |  | RevVlv | RevVlv
|  |  |  | AuxHtg | AuxHtg
|  |  |  | Mode | Mode
|  |  | Stage 1 | C1-S | C1-S
|  |  |  | C1 | C1 | On | [5 empty] | UCB C1 24 VAC output status
|  |  |  | C1-En | C1-En Yes | No | [5 empty] | Yes permits UCB C1 24 VAC output; independent of #ClgStgs selection, No does not permit UCB C1 24 VAC output
|  |  |  | C1OnTmr | C1OnTmr 0sec | [6 empty] | active number of minutes remaining for C1 minimum run timer expiration
|  |  |  | C1ASCDTmr | C1ASCDTmr 0sec | [6 empty] | active number of minutes remaining for C1 anti-short cycle delay timer expiration
|  |  |  | C1RunTim | C1RunTim .0 hr | 0 | through | ????? |  |  |  | accumulated run time of UCB C1 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EC1 | EC1 42.4 F | [6 empty] | the buffered UCB EC1 thermistor input
|  |  |  | CC1 | CC-1 96 F | [5 empty] | input to the UCB CC1 pins | the buffered UCB CC1 thermistor input
|  |  |  | SLP-1 | SLP-1 371.1psi | [5 empty] | FDD board present | the buffered FDD master SLP1 pressure transducer input
|  |  |  | LLP-1 | LLP-1 371.6psi | [5 empty] | FDD board present | the buffered FDD master LLP1 pressure transducer input
|  |  |  | SLT-1 | SLT-1 123.9 F | [5 empty] | FDD board present | the buffered FDD master SLT1 thermistor input
|  |  |  | LLT-1 | LLT-1 74.2 F | [5 empty] | FDD board present | the buffered FDD master LLT1 thermistor input
|  |  |  | C1-EI | C1-EI ? F | [5 empty] | FDD board present
|  |  |  | C1-CI | C1-CI ? F | [5 empty] | FDD board present
|  |  |  | C1-CondTempOvrAmb | C1-CondTempOvrAmb ? F | [5 empty] | FDD board present
|  |  |  | C1-EvapTempValue | C1-EvapTempValue ? F | [5 empty] | FDD board present
|  |  | Stage 2 | C2-S | C2-S Off-Idle
|  |  |  | C2 | C2 Off | On | [5 empty] | #ClgStgs = 2 or more | effective for units with 2 or more compressor cooling stages; UCB C2 24 VAC output status
|  |  |  | C2-En | C2-En Yes | No | [5 empty] | #ClgStgs = 2 or more | Yes permits UCB C2 24 VAC output; independent of #ClgStgs selection, No does not permit UCB C1 24 VAC output
|  |  |  | C2OnTmr | C2OnTmr 0sec | [6 empty] | #ClgStgs = 2 or more | active number of minutes remaining for C2 minimum run timer expiration
|  |  |  | C2ASCDTmr | C2ASCDTmr 0sec | [6 empty] | #ClgStgs = 2 or more | active number of minutes remaining for C2 anti-short cycle delay timer expiration
|  |  |  | C2RunTim | C2RunTim 0 hr | .0 hr | through | ????? |  |  |  | #ClgStgs = 2 or more | accumulated run time of UCB C2 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EC2 | EC2 132.0 F | [6 empty] | #ClgStgs = 2 or more | the buffered UCB EC2 thermistor input
|  |  |  | CC2 | CC-2 96 F | [5 empty] | input to the UCB CC2 pins | the buffered UCB CC2 thermistor input | the buffered UCB CC2 thermistor input
|  |  |  | SLP-2 | SLP-2 372.5psi | [5 empty] | FDD board present | the buffered FDD master SLP2 pressure transducer input
|  |  |  | LLP-2 | LLP-2 372.4psi | [5 empty] | FDD board present | the buffered FDD master LLP2 pressure transducer input
|  |  |  | SLT-2 | SLT-2 130.9 F | [5 empty] | FDD board present | the buffered FDD master SLT2 thermistor input
|  |  |  | LLT-2 | LLT-2 69.8 F | [5 empty] | FDD board present | the buffered FDD master LLT2 thermistor input
|  |  |  | C2-EI | C2-EI ? F | [5 empty] | FDD board present
|  |  |  | C2-CI | C2-CI ? F | [5 empty] | FDD board present
|  |  |  | C2-CondTempOvrAmb | C2-CondTempOvrAmb ? F | [5 empty] | FDD board present
|  |  |  | C2-EvapTempValue | C2-EvapTempValue ? F | [5 empty] | FDD board present
|  |  | Setup | Clg-En | Clg-En Yes | No | [5 empty] | sets permission to allow UCB C1 and C2, ( 4-stage board C3 and C4) 24 VAC outputs for compressor contactor coils; Yes permits C1, C2 (C3 & C4) output, No does not permit C1, C2 (C3 & C4) output
|  |  |  | Htg-En | Htg-En Yes | No
|  |  |  | MinRtCoolStg | MinRtCoolStg 3min | 3min | through | 10min |  |  |  | sets the minimum run time for C# outputs; individual C# minimum run time begins when the output is turned on ; unless interrupted by safety shutdown, output is mantained until the individual C# minimum run time expires | sets the minimum run time for C# outputs; individual C# minimum run time begins when the output is turned on ; unless interrupted by safety shutdown, output is mantained until the individual C# minimum run time expires
|  |  |  | LeadLag-En | LeadLag-En No | Yes | [5 empty] | effective for 2 or more compressor stages; Yes permits compressor equalized runtime where the C# output with the least C#RunTim operates first, the the C# output with the next least C#RunTim operates second, etc. No operates the C1 output first, the C2 output second, etc. | effective for 2 or more compressor stages; Yes permits compressor equalized runtime where the C# output with the least C#RunTim operates first, the the C# output with the next least C#RunTim operates second, etc. No operates the C1 output first, the C2 output second, etc.
|  |  |  | LowAmbFanPrerun | LowAmbFanPrerun 60sec | 0 sec | through | 255 sec |  |  |  | the amount of time the indoor blower must operate before compressor operation is permitted when OprOAT is below LowAmb10On5OffSp | the amount of time the indoor blower must operate before compressor operation is permitted when OprOAT is below LowAmb10On5OffSp
|  |  |  | ClgOATCutout-En | ClgOATCutout-En Yes | No | [5 empty] | Yes does not permit C# output if OprOAT falls below ClgOATCutout, No permits C# output at any OprOAT
|  |  |  | ClgOATCutout | ClgOATCutout 45 F | 0 F | through | 100 F |  |  |  | if ClgOATCutout-En = Yes, C# output is not permitted if OprOAT falls below this setpoint
|  |  |  | SATCoolLimit-En | SATCoolLimit-En Yes | No | [5 empty] | Yes does not permit C# output if SAT falls below SATCoolLimit-Sp, No permits C# output at any SAT
|  |  |  | SATCoolLimit-Sp | SATCoolLimit-Sp 50 F | 40 F | through | 65 F |  |  |  | if SATCoolLimit-En = Yes, C# output is not permitted if SAT falls below this setpoint
|  |  |  | SATHtgLimit-En | SATHtgLimit-En Yes | No | [5 empty] | Yes does not permit H# output if SAT rises above SATHtgLimit-Sp, No permits H# output at any SAT
|  |  |  | SATHtgLimit-Sp | SATHtgLimit-Sp | SATHtgLimit-Sp 135 F |  | 100 F | through | 180 F |  |  | if SATHtgLimit-En = Yes H# output is not permitted if SAT rises above this setpoint
|  |  |  | ClgAdapTunEn | ClgAdapTunEn Yes | No | [5 empty] | On enables the cooling cycle rate algorithm ; Off does not enable the cooling cycle rate algorithm
|  |  |  | HtgAdapTunEn | HtgAdapTunEn Yes | No | [5 empty] | On enables the heating cycle rate algorithm ; Off does not enable the heating cycle rate algorithm
|  |  |  | EconLoad-En | EconLoad-En No | Yes | [5 empty] | No does not permit economizer loading; effective if SATCoolLimit-En = Yes and OAT is above 60°F, Yes permits increased Econ position when all but one C# output has been cutoff due to SAT below SATCoolLimit-Sp
|  |  |  | AllCompOff-Econ | AllCompOff-Econ No | Yes |  |  |  |  | economizer board present | Yes does not permit compressor operation during free cooling; No permits compressor operation during free cooling
|  |  |  | LowAmb-En | LowAmb-En No | Yes | [5 empty] | Yes permits compressor operation to 0 F without 10 minute on and 5 minute off cycling
|  |  |  | LowAmb10On5OffSp | LowAmb10On5OffSp 45 F | 0 F | through | 60 F |  |  |  | if compressor operation otherwise is permitted, C# output cycled on 10 minutes/off 5 minutes with OprOAT below this setpoint
|  |  |  | TempHumCtrl-En | TempHumCtrl-En No | Yes | [5 empty] | No does not permit OprSH above TempHum-Sp to decrease OprCVClg-Sp, Yes permits OprSH above TempHum-Sp to decrease OprCVClg-Sp up to the amount set for MaxTempHumSpOff
|  |  |  | TempHum-Sp | TempHum-Sp 50 %H | 20 %H | through | 80 %H |  |  | TempHumCtrl = Yes | effective if TempHumCtrl-En = Yes; OprSH above this setpoint decreases OprCVClg-Sp up to the amount set for MaxTempHumSpOff
|  |  |  | MaxTempHumSpOff | MaxTempHumSpOff 3.0 F | .0 F | through | 5.0 F |  |  | TempHumCtrl = Yes | effective if TempHumCtrl-En = Yes; maximimum amount OprSH above TempHum-Sp decreases OprCVClg-Sp; 1/10th adjustment increments
|  |  |  | TempHumValPerDegOff | TempHumValPerDegOff 5 %H | 1 %H | through | 10 %H |  |  | TempHumCtrl = Yes | effective if TempHumCtrl-En = Yes; sets humidity increments of OprSH above TempHum-Sp to decrease OprCVClg-Sp by 1°F, up to the amount set for MaxTempHumSpOff; adjustment increments of 1s
|  | Econ | Status | Econ-S | Econ-S Disabled
|  |  |  | Econ | Econ 0% | [5 empty] | economizer board present | economizer board ECON 2-10 VDC output status
|  |  |  | Econ-Free | Econ-Free No | Yes |  |  |  |  | economizer board present | Yes indicates economizer free cooling is available, No indicates economizer free cooling is not availble; indication depends on FreeClg-Mode effective and current outdoor/indoor conditions
|  |  |  | FreeClg-Mode | FreeClg-Mode Dry Bulb Temperature | Dual Enthalpy | Single Enthalpy |  |  |  | economizer board present | free cooling changeover method currently effective; indication depends on FreeClg-Sel setting, presence of OAH 0-10 VDC input to the economizer board and presence of RAH 0-10 VDC input to the UCB
|  |  |  | MAT | MAT 71 F | Input Unreliable |  |  |  |  | economizer board present and input to the economizer MAT terminals | the buffered economizer board mat thermistor input; Input Unreliable indicates MAT input was once detected and is currently lost
|  |  |  | OA-Enth | OA-Enth 20 B/# | 0 B/# |  |  |  |  | economizer board present | enthalpy calculated from OAH 0-10 VDC input to the economizer board and OprOAT; 0B/# indicated if OAH 0-10 VDC input to the economizer board is not present
|  |  |  | OprOAH | 19 %H | Input Unreliable |  |  |  |  | economizer board present | the buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present
|  |  |  | OprOAT | OprOAT 70.0 F | [5 empty] | economizer board present | the buffered outdoor air temperature in use; may be from UCB OAT thermistor input or FC BUS communicated value sources
|  |  |  | RA-Enth | RA-Enth 0B/# | [5 empty] | economizer board present | enthalpy calculated from RAH 0-10 VDC input to the UCB and RAT thermistor input to the UCB; 0B/# indicated if RAH 0-10 VDC input to the UCB is not present
|  |  |  | RAH | RAH 19.6 %H | Input Unreliable |  |  |  |  | economizer board present and input to the UCB RAH pins | the buffered UCB RAH 0-10 VDC input; ?Unrel indicates UCB RAH 0-10 VDC input was once detected and is currently lost
|  |  |  | RAT | RAT 70.1 F | [5 empty] | economizer board present | the buffered UCB RAT thermistor input
|  |  |  | SAH | SAH 71 %H | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board SAH 0-10 VDC input; Input Unreliable indicates SAH input is currently not present
|  |  | Setup | Econ-En | Econ-En Yes | No |  |  |  |  | economizer board present | Yes permits economizer free cooling operation, No does not permit economizer free cooling operation
|  |  |  | FreeClg-Sel | FreeClg-Sel Auto | Dry Bulb Temperature | Single Enthalpy | Dual Enthalpy |  |  | economizer board present | sets the desired economizer free cooling changeover method; Auto sets the changever method based on the presence of economizer board OAH 2-10 VDC input and UCB RAH 2-10 VDC input, Dual Enthalpy requires OAH and RAH inputs to be effective, Single Enthalpy requires OAH input to be effective
|  |  |  | Econ-MinPos | Econ-MinPos 20% | 0% | through | 100% |  |  | economizer board present | economizer minimum position effective with occupied status, indoor blower operation and when OAT is above LowAmb-Sp
|  |  |  | EconOAT-SpEn | EconOAT-SpEn 55 F | 40 F | through | 80 F |  |  | economizer board present | dry bulb free cooling changeover setpoint; with FreeClg-Mode = Dry Bulb Tempe, economizer free cooling is available when OAT is below this setpoint
|  |  |  | EconOAEnth-Sp | EconOAEnth-Sp 27B/# | 10 B/# | through | 50 B/# |  |  | economizer board present | single enthalpy free cooling changeover setpoint; with FreeClg-Mode = Single Enthalpy, economizer free cooling is available when OA-Enth is below this setpoint
|  |  |  | LowAmb-Sp | LowAmb-Sp 0 F | 0 F | through | 60 F |  |  | economizer board present | with OprOAT below this setting LowAmb-MinPos is the effective economizer minimum position, with OprOAT below this setting Econ-MinPos is the effective economizer minimum position
|  |  |  | LowAmb-MinPos | LowAmb-MinPos 0 % | 0% | through | 100% |  |  | economizer board present | economizer minimum position effective with occupied status, indoor blower operation and when OAT is below LowAmb-Sp; typically set less than Econ-MinPos
|  |  |  | LowSpeedFan-MinPos | LowSpeedFan-MinPos 25% | [5 empty] | economizer board present | not to be used until setting access provisions are made in later control revisions, economizer minimum position effective with occupied status and when the VFD speed controlled indoor blower operates at the lowest setting; typically set greater than Econ-MinPos
|  |  |  | IAQEcon-MaxPos | IAQEcon-MaxPos 50 % | 0% | through | 100% |  |  | economizer board present | the maximum economizer actuator position for demand ventilation operation; termed "DVentMaxEconPos" elsewhere
|  |  |  | EconMechStp | EconMechStp Option B | Option A |  |  |  |  | economizer board present | Option A - economizer damper position and/or time triggers compressor operation to supplement free cooling; Option B - supply air temperature with VAV supply air temperature (upper/lower) setpoint triggers compressor operation to supplement free cooling
|  | PowerEx | Status | ExFan | ExFan Off | On |  |  |  |  | economizer board present | economizer board EX-FAN 24 VAC output status
|  |  |  | ExFanVFD | ExFanVFD 0 % | [5 empty] | economizer board present and ExFType = Variable Frequency Fan | effective for Variable Frequency Fan power exhaust; the economizer board EX VFD 2-10 VDC output status
|  |  |  | ExFanVFDFlt | ExFanVFDFlt Normal | Alarm |  |  |  |  | economizer board present and ExFType = Variable Frequency Fan | economizer board EX VFD FLT 24 VAC input status; Normal indicates 0 VAC input to the EX VFD FLT pin, Alarm indicates 24 VAC input to the EX VFD FLT pin
|  |  |  | ExFan-RT | ExFan-RT .0 hr | .0 hr | through | ????? |  |  | economizer board present | accumulated run time of economizer board EX-FAN 24 VAC output; resetable in 1/10th adjustment increments; ????? shown on UCB display indicates greater than 999.9 hours of accumulated run time
|  |  |  | EAD-O | EAD-O 0 % | [5 empty] | economizer board present and ExFType = Modulating Damper | effective for Modulating Damper power exhaust; the economizer board EX VFD 2-10 VDC output status
|  |  |  | BldgPres | BldgPres -.011"/w | Input Unreliable |  |  |  |  | economizer board present and ExFType = Non modulating Damper | effective for Modulating Damper and Variable Frequency Fan power exhaust; the buffered economizer board BLDG PRES 0-5 VDC input; ?Unrel indicates BLDG PRS input is currently not present
|  |  |  | Bldg-Sp | Bldg-Sp .100"/w | -.249"/w | through | .249"/w |  |  | economizer board present and ExFType = Non modulating Damper | effective for Modulating Damper and Variable Frequency Fan power exhaust; building pressure setpoint for exhaust damer position/exhaust fan VFD speed control; 1/100th adjustment increments
|  |  | Setup | ExFType | ExFType None | Non-modulating | Modulating Damper | Variable Frequency Fan |  |  | economizer board present | power exhaust fan mode selection; None = no power exhaust fan installed, Non-Modulating = power exhaust fan on/off by economizer position, (Modulating Damper = power exhaust fan on/off by exhaust damper position, exhaust damper position by BLDG PRES input), (Variable Frequency Fan = power exhaust fan VFD speed control by BLDG PRES input)
|  |  |  | EconDmpPosFanOn | EconDmpPosFanOn 60 % | 20% | through | 99% |  |  | economizer board present and ExFType ≠ Non modulating | effective for Non-Modulating power exhaust; the Econ position where the economizer board EX-FAN 24 VAC output is turned On; must be set greater than EconDmpPosFanOff
|  |  |  | EconDmpPosFanOff | EconDmpPosFanOff 20 % | 10% | through | 89% |  |  | economizer board present and ExFType ≠ Non modulating | effective for Non-Modulating power exhaust; the Econ position where the economizer board EX-FAN 24 VAC output is turned Off; must be set greater than Econ-MinPos and less than EconDmpPosFanOff
|  |  |  | ExDmpPosFanOn | ExDmpPosFanOn 80 % | 20% | through | 99% |  |  | economizer board present and ExFType = Modulating Damper | effective for Modulating Damper power exhaust; the EAD-O position where the economizer board EX-FAN 24 VAC output is turned On; must be set greater than ExDmpPosFanOff
|  |  |  | ExDmpPosFanOff | ExDmpPosFanOff 20 % | 10% | through | 89% |  |  | economizer board present and ExFType = Modulating Damper | effective for Modulating Damper power exhaust; the EAD-O position where the economizer board EX-FAN 24 VAC output is turned Off; must be set less than ExDmpPosFanOn
|  |  |  | ERV-En | ERV-En No | Yes |  |  |  |  | economizer board present | Yes sets economizer and power exhaust operation to integrate an exhaust recovery ventilator
|  |  |  | ERVUnoccFan-En | ERVUnoccFan-En No | Yes |  |  |  |  | economizer board present | Yes permits ERV operation during Unoccupied mode; No does not permit ERV operation during Unoccupied mode
|  | Dvent | DVent-Mode | Dvent-Mode Disabled |  | Controlled by IAQ | Diff between IAQ and OAQ |  |  |  | economizer board present | Demand Ventilation mode selection; Disabled permits no demand ventilation function, Controlled by IAQ requires IAQ input, Diff between IAQ and OAQ requires IAQ and OAQ inputs
|  |  | OprIAQ | OprIAQ 489ppm |  | Input Unreliable |  |  |  |  | economizer board present | the buffered indoor air quality in use; may be from economizer board IAQ 0-10 VDC input, SA BUS NetSensor or FC BUS communicated value sources; ?Unrel indicates IAQ input is currently not present
|  |  | DVentMaxEconPos | DVentMaxEconPos 50% |  | 0% | through | 100% |  |  | economizer board present | the maximum economizer actuator position for demand ventilation operation; termed "IAQEcon-MaxPos" elsewhere
|  |  | DVentIAQ-Sp | DVentIAQ-Sp 1000ppm |  | 0ppm | through | 5000ppm |  |  | economizer board present | effective when DVent-Mode = Controlled by IAQ; with occupied status and indoor blower operation, demand ventilation operation the economizer is initiated if OprIAQ rises above this setpoint; adjustment increments of 1s
|  |  | DVentDiff-Sp | DVentDiff-Sp 600ppm |  | 0ppm | through | 5000ppm |  |  | economizer board present | effective when DVent-Mode = Diff between IAQ and OAQ; with occupied status and indoor blower operation, demand ventilation operation the economizer is initiated if OprIAQ rises above OprOAQ plus this setpoint; adjustment increments of 1s
|  |  | IAQRange | IAQRange 2000ppm |  | 0ppm | through | 5000ppm |  |  | economizer board present | setting only required when a CO₂ sensor is connected to the economizer board IAQ 0-10 VDC input; set for the CO₂ ppm measured at 10 VDC IAQ sensor output; adjustment increments of 1s
|  |  | OAQRange | OAQRange 2000ppm |  | 0ppm | through | 5000ppm |  |  | economizer board present | setting only required when a CO₂ sensor is connected to the economizer board OAQ 0-10 VDC input; set for the CO₂ ppm measured at 10 VDC OAQ sensor output; adjustment increments of 1s
|  | AirMonStation | MOAFlow-Sp | MOAFlow-Sp 10CFM |  | 0CFM | through | 100CFM |  |  | economizer board present | 3rd-party air monitoring station accessory required; the minimum outdoor air flow setpoint, effective with occupied status and indoor blower operation; economizer actuator position increased if Fr Air falls below this setpoint and decreased if Fr Air rises above this setpoint; adjustment increments of 1s
|  |  | Fr Air | Fr Air 7CFM |  | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board FR AIR 0-10 VDC input; ?Unrel indicates FR AIR input is currently not present
|  |  | MOA-Range | MOA-Range 10000CFM |  | 0CFM | through | 50000CFM |  |  | economizer board present | set for the CFM measured at 10 VDC MOA sensor output; adjustment increments of 1s
|  | HGR | HGR-S | HGR-S Off-Idle
|  |  | HGR | HGR Off |  | On |  |  |  |  | HGR-En = On
|  |  | HGRHum-Sp | HGRHum-Sp 60 %H |  | 0 | through | 100% |  |  | HGR-En = On | effective for hot gas reheat operation when Occupied; hot gas reheat operation is initiated when OprSH rises above this setpoint
|  |  | HGRUnoccHum-SP | HGRUnoccHum-SP 70 % |  | 0% | through | 100% |  |  | HGR-En = On | effective for hot gas reheat operation when UnOccupied; hot gas reheat operation is initiated when OprSH rises above this setpoint
|  |  | HGR-En | HGR-En No |  | Yes |  |  |  |  | HGR-En = On in Details>Service>Factory | Yes sets permission to allow hot gas reheat operation, No does not permit hot gas reheat operation
|  |  | HGRAlt-En | HGRAlt-En No |  | Yes |  |  |  |  | HGR-En = On | Yes sets either the Normal or Alternate hot gas reheat sequence
|  |  | HGRAltWrite | HGRAltWrite Yes |  | No |  |  |  |  | HGR-En = On | Yes sets permission to allow access to hot gas reheat mode selection in HGRAlt-En; No does not permit access to hot gas reheat mode selection in HGRAlt-En
|  |  | HGRUnocc-En | HGRUnocc-En Yes |  | No |  |  |  |  | HGR-En = On | Yes sets permission to allow hot gas reheat operation when occupancy status is UnOccupied, No does not permit hot gas reheat operation when occupancy status is UnOccupied
|  | SmokeCtrl | OprPurgeCmd | OprPurgeCmd False |  | True |  |  |  |  | economizer board present | False indicates a purge command is not currently active, True indicates a purge command is currently active
|  |  | PurgeCmdSrc | PurgeCmdSrc Return Air Temp |  | Local Input | BAS Override |  |  |  | economizer board present | Return Air indicates the purge command source is 24 VAC input to the economizer board PUR terminal, BAS Override is from FC BUS communicated command
|  |  | Purge | Purge False |  | True |  |  |  |  | economizer board present | economizer board PUR input status; True indicates 24 VAC input to the PUR teminal, False indicates 0 VAC input to the PUR teminal
|  |  | NetPurge | NetPurge Value Timed Out |  | True | False |  |  |  | economizer board present | status of the FC BUS communicated purge command; True indicates a communicated purge command is active, False indicates a communicated purge command is not active but FC BUS communication is present, ?Unrel indicates FC BUS communication for the purge command is not present
|  |  | SD | SD Normal |  | Alarm | [5 empty] | UCB SD 24 VAC input status; Normal indicates 24 VAC input to the SD terminal, Alarm indicates 0 VAC input to the SD terminal
| Service | Inputs | Sensors | ST | ST 80.5 F | Input Unreliable |  |  |  |  | input to the UCB ST terminal | the buffered UCB ST thermistor input
|  |  |  | SSO | SSO .0 F | Input Unreliable |  |  |  |  | input to the UCB SSO terminal | the buffered UCB SSO 0-20,000 Ω input
|  |  |  | IAQ | IAQ 488ppm | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board IAQ 0-10 VDC input; ?Unrel indicates IAQ input is currently not present
|  |  |  | RAH | RAH No Input | Input Unreliable |  |  |  |  | input to the UCB RAH pins | the buffered UCB RAH 0-10 VDC input; ?Unrel indicates UCB RAH 0-10 VDC input was once detected and is currently lost
|  |  |  | OAT | OAT 31.6 F | [6 empty] | the buffered UCB OAT thermistor input
|  |  |  | OAH | OAH No Input | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board OAH 0-10 VDC input; ?Unrel indicates OAH input is currently not present
|  |  |  | OAQ | OAQ 195ppm | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board OAQ 0-10 VDC input; ?Unrel indicates OAQ input is currently not present
|  |  |  | SAT | SAT 80.7 F | [6 empty] | the buffered UCB SAT thermistor input
|  |  |  | RAT | RAT 78.3 F | [6 empty] | the buffered UCB RAT thermistor input
|  |  |  | SAH | SAH No Input | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board SAH 0-10 VDC input; ?Unrel indicates SAH input is currently not present
|  |  |  | DctPrs | DctPrs Not Present | [5 empty] | FanCtl-Type = Variable Speed | effective for VAV units; the buffered UCB DCT PRS 0-5 VDC input
|  |  |  | BldgPres | BldgPres No Input | Input Unreliable |  |  |  |  | economizer board present and ExFType ≠ Non modulating | effective for Modulating Damper and Variable Frequency Fan power exhaust; the buffered economizer board BLDG PRES 0-5 VDC input; ?Unrel indicates BLDG PRS input is currently not present
|  |  |  | MAT | MAT No Input | Input Unreliable |  |  |  |  | economizer board present and input to the economizer MAT terminals | the buffered economizer board mat thermistor input; ?Unrel indicates MAT input was once detected and is currently lost
|  |  |  | Fr Air | Fr Air 6CFM | Input Unreliable |  |  |  |  | economizer board present | the buffered economizer board FR AIR 0-10 VDC input; ?Unrel indicates FR AIR input is currently not present
|  |  |  | UCB24VForOutp | UCB24VForOutp 26.2VAC | [6 empty] | the VAC measured at the UCB 24V FOR OUTPUTS terminal
|  |  |  | EconDampPos | EconDampPos 0 | Input Unreliable |  |  |  |  | economizer board present | the economizer board AI-IN 0-10 VDC input; ?Unrel indicates AI-IN input is currently not present
|  |  | CoilSensors | EC1 | EC1 42.6 F | [6 empty] | the buffered UCB EC1 thermistor input
|  |  |  | CC1 | CC1 No Input | [5 empty] | input to the UCB CC1 pins | the buffered UCB CC1 thermistor input
|  |  |  | EC2 | EC2 Not Present | [5 empty] | #ClgStgs = 2 or more | the buffered UCB EC2 thermistor input
|  |  |  | CC2 | CC2 Not Present | [5 empty] | input to the UCB CC2 pins | the buffered UCB CC2 thermistor input
|  |  |  | EC3 | EC3 Not Present | [5 empty] | #ClgStgs = 3 or more | the buffered UCB EC3 thermistor input
|  |  |  | CC3 | CC3 Not Present | [5 empty] | input to the UCB CC3 pins | the buffered UCB CC3 thermistor input
|  |  |  | EC4 | EC4 Not Present | [5 empty] | #ClgStgs = 4 or more | the buffered UCB EC4 thermistor input
|  |  |  | CC4 | CC4 Not Present | [5 empty] | input to the UCB CC4 pins | the buffered UCB CC4 thermistor input
|  |  | Thermostat | Y1-Tstat | Y1-Tstat Off | On | [5 empty] | UCB Y1 24 VAC input status; On indicates 24 VAC input to the Y1 terminal, Off indicates 0 VAC input to the Y1 terminal
|  |  |  | Y2-Tstat | Y2-Tstat Off | On |  |  |  |  | #ClgStgs = 2 or more | UCB Y2 24 VAC input status; On indicates 24 VAC input to the Y2 terminal, Off indicates 0 VAC input to the Y2 terminal; though this parameter is not displayed if #ClgStgs = 1, Y2 input remains effective to initiate compressor operation to supplement free cooling for single-compressor units
|  |  |  | Y3-Tstat | Y3-Tstat Off | On |  |  |  |  | #ClgStgs = 3 or more | UCB Y3 24 VAC input status; On indicates 24 VAC input to the Y3 terminal, Off indicates 0 VAC input to the Y3 terminal; though this parameter is not displayed if #ClgStgs = 1 or 2, Y3 input remains effective to initiate compressor operation to supplement free cooling for single-compressor units
|  |  |  | Y4-Tstat | Y4-Tstat Off | On |  |  |  |  | #ClgStgs = 4 or more | UCB Y4 24 VAC input status; On indicates 24 VAC input to the Y4 terminal, Off indicates 0 VAC input to the Y4 terminal; though this parameter is not displayed if #ClgStgs = 1,2 or 3, Y4 input remains effective to initiate compressor operation to supplement free cooling for single-compressor units
|  |  |  | W1-Tstat | W1-Tstat Off | On | [5 empty] | UCB W1 24 VAC input status; On indicates 24 VAC input to the W1 terminal, Off indicates 0 VAC input to the W1 terminal
|  |  |  | W2-Tstat | W2-Tstat Off | On |  |  |  |  | #HtgStgs = 2 or more | UCB W2 24 VAC input status; On indicates 24 VAC input to the W2 terminal, Off indicates 0 VAC input to the W2 terminal
|  |  |  | W3-Tstat | W3-Tstat Off | On |  |  |  |  | #HtgStgs = 3 or more | UCB W3 24 VAC input status; On indicates 24 VAC input to the W3 terminal, Off indicates 0 VAC input to the W3 terminal
|  |  |  | G-Tstat | G-Tstat Off | On | [5 empty] | UCB G 24 VAC input status; On indicates 24 VAC input to the G terminal, Off indicates 0 VAC input to the G terminal
|  |  |  | Tstat-Only | Tstat-Only Yes | No | [5 empty] | Yes permits only thermostat inputs to initiate comfort control requests for heating, cooling and indoor blower operation; scheduling and comfort control by sensor inputs are disabled
|  |  | BinaryInputs | Limit | Limit Normal | Alarm | [5 empty] | UCB LIMIT 24 VAC input status; Normal indicates 24 VAC input to the LIMIT terminal, Alarm indicates 0 VAC input to the LIMIT terminal
|  |  |  | Lim2 | Lim2 Normal | Alarm |  |  |  |  | 4-stage board present | 4-stage board Lim2 24 VAC input status; Normal indicates 24 VAC input to the Lim2 terminal, Alarm indicates 0 VAC input to the Lim2 terminal
|  |  |  | Lim3 | Lim3 Normal | Alarm |  |  |  |  | 4-stage board present | 4-stage board Lim3 24 VAC input status; Normal indicates 24 VAC input to the Lim3 terminal, Alarm indicates 0 VAC input to the Lim3 terminal
|  |  |  | MV | MV Off | On | [5 empty] | UCB MV 24 VAC input status; Yes indicates 24 VAC input to the MV pin, No indicates 0 VAC input to the MV pin
|  |  |  | GV2 | GV2 Off | On |  |  |  |  | 4-stage board present | 4-stage board GV2 24 VAC input status; Normal indicates 24 VAC input to the GV2 terminal, Alarm indicates 0 VAC input to the GV2 terminal
|  |  |  | GV3 | GV3 Off | On |  |  |  |  | 4-stage board present | 4-stage board GV3,4 24 VAC input status; Normal indicates 24 VAC input to the GV3,4 terminal, Alarm indicates 0 VAC input to the GV3,4 terminal
|  |  |  | HPS1 | HPS1 Normal | Alarm | [5 empty] | UCB HPS1 24 VAC input status; Normal indicates 24 VAC input to the HPS1 pin, Alarm indicates 0 VAC input to the HPS1 pin
|  |  |  | LPS1 | LPS1 Normal | Alarm | [5 empty] | UCB LPS1 24 VAC input status; Normal indicates 24 VAC input to the LPS1 pin, Alarm indicates 0 VAC input to the LPS1 pin
|  |  |  | FS1 | FS1 Normal | Alarm | [5 empty] | refrigerant circuit #1 evaporator coil freeze protection status; Normal indicates EC1 above Freeze-Sp, Alarm indicates EC1 below Freeze-Sp
|  |  |  | HPS2 | HPS2 Normal | Alarm |  |  |  |  | #ClgStgs = 2 or more | UCB HPS2 24 VAC input status; Normal indicates 24 VAC input to the HPS2 pin, Alarm indicates 0 VAC input to the HPS2 pin
|  |  |  | LPS2 | LPS2 Normal | Alarm |  |  |  |  | #ClgStgs = 2 or more | UCB LPS2 24 VAC input status; Normal indicates 24 VAC input to the LPS2 pin, Alarm indicates 0 VAC input to the LPS2 pin
|  |  |  | FS2 | FS2 Normal | Alarm |  |  |  |  | #ClgStgs = 2 or more | refrigerant circuit #2 evaporator coil freeze protection status; Normal indicates EC2 above Freeze-Sp, Alarm indicates EC2 below Freeze-Sp
|  |  |  | HPS3 | HPS3 Normal | Alarm |  |  |  |  | #ClgStgs = 3 or more | UCB HPS3 24 VAC input status; Normal indicates 24 VAC input to the HPS3 pin, Alarm indicates 0 VAC input to the HPS3 pin
|  |  |  | LPS3 | LPS3 Normal | Alarm |  |  |  |  | #ClgStgs = 3 or more | UCB LPS3 24 VAC input status; Normal indicates 24 VAC input to the LPS3 pin, Alarm indicates 0 VAC input to the LPS3 pin
|  |  |  | FS3 | FS3 Normal | Alarm |  |  |  |  | #ClgStgs = 3 or more | refrigerant circuit #3 evaporator coil freeze protection status; Normal indicates EC3 above Freeze-Sp, Alarm indicates EC3 below Freeze-Sp
|  |  |  | HPS4 | HPS4 Normal | Alarm |  |  |  |  | #ClgStgs = 4 or more | UCB HPS4 24 VAC input status; Normal indicates 24 VAC input to the HPS4 pin, Alarm indicates 0 VAC input to the HPS4 pin
|  |  |  | LPS4 | LPS4 Normal | Alarm |  |  |  |  | #ClgStgs = 4 or more | UCB LPS4 24 VAC input status; Normal indicates 24 VAC input to the LPS4 pin, Alarm indicates 0 VAC input to the LPS4 pin
|  |  |  | FS4 | FS4 Normal | Alarm |  |  |  |  | #ClgStgs = 4 or more | refrigerant circuit #4 evaporator coil freeze protection status; Normal indicates EC4 above Freeze-Sp, Alarm indicates EC4 below Freeze-Sp
|  |  |  | FanOvrload | FanOvrload Normal | Alarm | [5 empty] | UCB FAN OVR 24 VAC input status; Normal indicates 24 VAC input to the FAN OVR pin, Alarm indicates 0 VAC input to the FAN OVR pin
|  |  |  | APS | APS Off | On | [5 empty] | UCB APS 24 VAC input status; Off indicates 0 VAC input to the APS pin, On indicates 24 VAC input to the APS pin
|  |  |  | DFS | DFS Normal | Alarm | [5 empty] | UCB DFS 24 VAC input status; Normal indicates 0 VAC input to the DFS pin, Alarm indicates 24 VAC input to the DFS pin
|  |  |  | SD | SD Normal | Alarm | [5 empty] | UCB SD 24 VAC input status; Normal indicates 24 VAC input to the SD terminal, Alarm indicates 0 VAC input to the SD terminal
|  |  |  | Purge | Purge False | True |  |  |  |  | economizer board present | economizer board PUR input status; True indicates 24 VAC input to the PUR teminal, False indicates 0 VAC input to the PUR teminal
|  |  |  | ExFanVFDFlt | ExFanVFDFlt Normal | Alarm |  |  |  |  | economizer board present and ExFType = Variable Frequency Fan | economizer board EX VFD FLT 24 VAC input status; Normal indicates 0 VAC input to the EX VFD FLT pin, Alarm indicates 24 VAC input to the EX VFD FLT pin
|  |  |  | FanVFDFlt | FanVFDFlt Normal | Alarm |  |  |  |  | FanCtl-Type = Fixed Variable or Variable Speed | UCB VFD FLT 24 VAC input status; Normal indicates 0 VAC input to the VFD FLT pin, Alarm indicates 24 VAC input to the VFD FLT pin
|  |  |  | OCC | OCC Unoccupied | Occupied | [5 empty] | effctive if OccMode = External, UCB OCC 24 VAC input status; Occupied indicates 24 VAC input to the OCC terminal, Unoccupied indicates 0 VAC input to the OCC terminal
|  |  |  | TempOCC | TempOCC True | False | [5 empty] | Temporary occupancy input status from a space temperature sensor, NetSensor or BAS communicated value
|  |  | Safeties | HPS1-Lo | HPS1-LO Normal | Lockout | [5 empty] | status of refrigerant circuit #1 high pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | LPS1-LO | LPS1-LO Normal | Lockout | [5 empty] | status of refrigerant circuit #1 low pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | FS1-LO | FS1-LO Normal | Lockout | [5 empty] | status of refrigerant circuit #1 evaporator freeze protection hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lokout is active
|  |  |  | HPS2-Lo | HPS2-LO Normal | Lockout |  |  |  |  | #ClgStgs = 2 or more | status of refrigerant circuit #2 high pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | LPS2-LO | LPS2-LO Normal | Lockout |  |  |  |  | #ClgStgs = 2 or more | status of refrigerant circuit #2 low pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | FS2-LO | FS2-LO Normal | Lockout |  |  |  |  | #ClgStgs = 2 or more | status of refrigerant circuit #2 evaporator freeze protection hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lokout is active
|  |  |  | HPS3-Lo | HPS3-LO Normal | Lockout |  |  |  |  | #ClgStgs = 3 or more | status of refrigerant circuit #3 high pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | LPS3-LO | LPS3-LO Normal | Lockout |  |  |  |  | #ClgStgs = 3 or more | status of refrigerant circuit #3 low pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | FS3-LO | FS3-LO Normal | Lockout |  |  |  |  | #ClgStgs = 3 or more | status of refrigerant circuit #3 evaporator freeze protection hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | HPS4-Lo | HPS4-LO Normal | Lockout |  |  |  |  | #ClgStgs = 4 or more | status of refrigerant circuit #4 high pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | LPS4-LO | LPS4-LO Normal | Lockout |  |  |  |  | #ClgStgs = 4 or more | status of refrigerant circuit #4 low pressure hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | FS4-LO | FS4-LO Normal | Lockout |  |  |  |  | #ClgStgs = 4 or more | status of refrigerant circuit #4 evaporator freeze protection hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | LimitLo | LimitLO Normal | Lockout | [5 empty] | status of UCB LIMIT 24 VAC input status hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | Lim2LO | Lim2LO Normal | Lockout |  |  |  |  | 4-stage board present | status of 4-stage board Lim2 24 VAC input status hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  |  | Lim3LO | Lim3LO Normal | Lockout |  |  |  |  | 4-stage board present | status of 4-stage board Lim3 24 VAC input status hard lockout; Normal indicates a hard lockout is not active, Lockout indicates a hard lockout is active
|  |  | NetworkInputs | NetST | NetST Value Timed Out | 40.0 F | through | 100.0 F |  |  |  | FC BUS communicated space temperature value; ?Unrel indicates FC BUS communication for the space temperature value is not present
|  |  |  | NetSSO | NetSSO Value Timed Out | -5.0 F | through | 5.0 F |  |  |  | FC BUS communicated space setpoint offset value; ?Unrel indicates FC BUS communication for the space setpoint offset value is not present
|  |  |  | NetSH | NetSH Value Timed Out | .0 %H | through | 100.0 %H |  |  |  | FC BUS communicated space humidity value; ?Unrel indicates FC BUS communication for the space humidity value is not present
|  |  |  | NetOcc | NetOcc Not Set | Occupied | UnOccupied |  |  |  |  | FC BUS communicated occupancy status; Occupied indicates a communicated occupied value is active, UnOccupied indicates a communicated unoccupied value is active, Not Set indicates an FC BUS communicated occupied/unoccupied value is not present
|  |  |  | NetTempOcc | NetTempOcc False | True | [5 empty] | FC BUS communicated temporary occupancy command; True indicates a communicated temporary occupancy command is active, False indicates a communicated temporary occupancy command is not active
|  |  |  | NetIAQ | NetIAQ Value Timed Out | 0ppm | through | 5000ppm |  |  | economizer board present | FC BUS communicated indoor air quality value; ?Unrel indicates FC BUS communication for the indoor air quality value is not present
|  |  |  | NetFanReq | NetFanReq Value Timed Out | On | Off |  |  |  |  | status of the FC BUS communicated request for indoor blower operation; On indicates a communicated request is active, Off indicates a commincated request is not active but FC BUS communication is present, ?Unrel indicates FC BUS communication for the request for indoor blower operation is not present
|  |  |  | NetOAT | NetOAT Value Timed Out | .0 F | through | 125.0 F |  |  |  | FC BUS communicated outdoor air temperature value; ?Unrel indicates FC BUS communication for the outdoor air temperature value is not present
|  |  |  | NetOAH | NetOAH Value Timed Out | .0 %H | through | 100.0 %H |  |  | economizer board present | FC BUS communicated outdoor air humidity value; ?Unrel indicates FC BUS communication for the outdoor air humidity value is not present
|  |  |  | NetOAQ | NetOAQ Value Timed Out | 0ppm | through | 50000ppm |  |  | economizer board present | FC BUS communicated outdoor air quality value; ?Unrel indicates FC BUS communication for the outdoor air quality value is not present
|  |  |  | NetPurge | NetPurge Value Timed Out | True | False |  |  |  | economizer board present | status of the FC BUS communicated purge command; True indicates a communicated purge command is active, False indicates a communicated purge command is not active but FC BUS communication is present, ?Unrel indicates FC BUS communication for the purge command is not present
|  |  |  | DirLoadshd | DirLoadshd No | Yes | [5 empty] | California Title 24 function
|  |  |  | Redline | Redline No | Yes | [5 empty] | California Title 24 function
|  |  |  | LoadShedEnable | LoadShedEnable No | Yes | [5 empty] | California Title 24 function
|  |  |  | LoadShedRateLim | LoadShedRateLim .066 | 0 | through | 1 |  |  |  | California Title 24 function
|  |  |  | LoadShedAdjust | LoadShedAdjust 4.0 F | 0 | through | 8 |  |  |  | California Title 24 function
|  | Outputs | Relay | C1 | C1 Off | On | [5 empty] | UCB C1 24 VAC output status
|  |  |  | C2 | C2 Off | On |  |  |  |  | #ClgStgs = 2 or more | effective for units with 2 or more compressor cooling stages; UCB C2 24 VAC output status
|  |  |  | C3 | C3 Off | On |  |  |  |  | #ClgStgs = 3 or more | effective for units with 3 or more compressor cooling stages; UCB C3 24 VAC output status
|  |  |  | C4 | C4 Off | On |  |  |  |  | #ClgStgs = 4 or more | effective for units with 4 or more compressor cooling stages; UCB C4 24 VAC output status
|  |  |  | H1 | H1 Off | On |  |  |  |  | #HtgStgs = 1 or more | effective for units with 1 or more heating stages; UCB H1 24 VAC output status
|  |  |  | H2 | H2 Off | On |  |  |  |  | #HtgStgs = 2 or more | effective for units with 2 or more heating stages; UCB H2 24 VAC output status
|  |  |  | H3 | H3 Off | On |  |  |  |  | #HtgStgs = 3 or more | effective for units with 3 or more heating stages; UCB H3 24 VAC output status
|  |  |  | ExFan | ExFan Off | On |  |  |  |  | economizer board present | economizer board EX-FAN 24 VAC output status
|  |  |  | CN-Fan | CN-Fan Off | On | [5 empty] | UCB CN-FAN 24 VAC output status
|  |  |  | CF2 | CF2 Off | On |  |  |  |  | 4-stage board present | 4-stage board CF2 output status
|  |  |  | Fan | Fan Off | On | [5 empty] | UCB FAN 24 VAC output status
|  |  |  | VAV Box | VAV Box Off | On |  |  |  |  | 4-stage board present | 4-stage VAV BOX 24 VAC contact
|  |  |  | HGR | HGR Off | On |  |  |  |  | HGR-En = On | UCB AUX HGR 24 VAC output status
|  |  |  | X-Out | X-Out Off | On | [5 empty] | UCB X terminal 24 VAC output status
|  |  | Analog | FanVFD | FanVFD 0 % | [5 empty] | FanCtl-Type ≠ Single Speed | UCB VFD 2-10 VDC output status
|  |  |  | Econ | Econ 0 % | [5 empty] | economizer board present | economizer board ECON 2-10 VDC output status
|  |  |  | ExFanVFD | ExFanVFD 0 % | [5 empty] | economizer board present and ExFType = Variable Frequency Fan | effective for Variable Frequency Fan power exhaust; the economizer board EX VFD 2-10 VDC output status
|  |  |  | HWV | HWV 0 % | [5 empty] | 4-stage board present | 4-stage board 2-10 VDC output status
|  | Factory | Standard | #ClgStgs | #ClgStgs 2 | 1 | through | 4 |  |  |  | number of compressor cooling stages; 1 or more enables the UCB C1 24 VAC output, 2 or more enables the UCB C2 24 VAC output, (3 or more enables the 4-stage board C3 24 VAC output, 4 enables the 4-stage board C4 24 VAC output)
|  |  |  | #HtgStgs | #HtgStgs 0 | 0 | through | 3 |  |  |  | number of heating stages; 1 or more enables the UCB H1 24 VAC output, 2 or more enables the UCB H2 24 VAC output, (3 enables the 4-stage board H3 24 VAC output)
|  |  |  | #HtPumpStgs | #HtPumpStgs 0 | 0 | through | 2 |  |  |  | number of heat pump stages; 1 or more enabled the UCB H1 VAC output to position reversing valve, 2 or more enabled the UCB H2 VAC output to initiate supplemental heat
|  |  |  | #RefrigSys | #RefrigSys 4 | 0 | through | 4 |  |  |  | only effective if #HtPumpStgs ≠ 0, number of refrigerant circuits in the unit
|  |  |  | Htg-Type | Htg-Type Staged | Proportional | [5 empty] | sets heating control method; Staged permits UCB H1, H2 (& 4-stage board H3) 24 VAC outputs, (not to be used until provivions are made in later control revisions, Proportional permits 4-stage board MOD HT 2-10 VDC output)
|  |  |  | FanCtl-Type | FanCtl-Type Single Speed | Two Speed | Fixed Variable | Variable Speed |  |  |  | indoor blower and unit operating mode selection; Single Speed = CV unit w/o indoor blower VFD, (Two Speed = CV unit w/2-step indoor blower VFD speed control), Fixed Variable = CV unit w/IntelliSpeed indoor blower VFD speed control, Variable Speed = VAV unit w/supply duct static/indoor blower VFD speed control
|  |  |  | ExFType | ExFType None | Non-modulating | Modulating Damper | Variable Frequency Fan |  |  | economizer board present | power exhaust fan mode selection; None = no power exhaust fan installed, Non-Modulating = power exhaust fan on/off by economizer position, (Modulating Damper = power exhaust fan on/off by exhaust damper position, exhaust damper position by BLDG PRES input), (Variable Frequency Fan = power exhaust fan VFD speed control by BLDG PRES input)
|  |  |  | APSSetup | APSSetup None | Constant Volume | Variable Volume |  |  |  |  | sets air proving switch presence and interaction with heating/cooling staging; None permits heating/cooling staging without 24 VAC input to the UCB APS pin, Constant Volume permits heating/cooling staging when APS = On, Variable Volume permits heating/cooling staging when APS = On or when DctPrs is greater than 0.20" wc
|  |  |  | HGR-En | HGR-En No | Yes | [5 empty] | Yes sets permission to allow hot gas reheat operation, No does not permit hot gas reheat operation
|  |  |  | HGP-Inst | HGP-Inst No | Yes | [5 empty] | set to Yes when refrigerant circuit #1 has hot gas bypass option, C1 is the first compressor cooling output on/last compressor output off if FanVFD is less than 50%
|  |  |  | BASCom | BASCom BACnet | Not Installed | [5 empty] | BACnet indicated with communication sub-board option
|  |  |  | Freeze-Sp | Freeze-Sp 26.0 F | 20.1 F | through | 31.9 F |  |  |  | setpoint for evaporator freeze protection of all refrigerant circuits; C# output is not permitted if CC# falls below this setpoint; 1/10th adjustment increments
|  |  |  | DFSInst | DFSInst Yes | No | [5 empty] | Yes produces dirty filter switch alarms when 24 VAC is received at DFS pin, No does not produce dirty filter switch alarms when 24 VAC is received at DFS pin
|  |  |  | FanOnDlyCool | FanOnDlyCool 0sec | 0sec | through | 30sec |  |  |  | the amount of time indoor blower operation is delayed following the initiation of cooling operation
|  |  |  | FanOffDlyCool | FanOffDlyCool 30sec | 0sec | through | 255sec |  |  |  | the amount of time indoor blower operation is maintained following the termination of cooling operation
|  |  |  | FanOnDlyHeat | FanOnDlyHeat 30sec | 0sec | through | 30sec |  |  |  | the amount of time indoor blower operation is delayed following 24 VAC input to the UCB MV pin being received; must be set to 0 for unit with electric heat
|  |  |  | FanOffDlyHeat | FanOffDlyHeat 60sec | 0sec | through | 255sec |  |  |  | the amount of time indoor blower operation is maitained following 24 VAC input to the UCB MV pin being lost
|  |  |  | LowAmb-En | LowAmb-En No | Yes | [5 empty] | Yes permits compressor operation to 0 F without 10 minute on and 5 minute off cycling
|  |  |  | LowAmbFanPrerunCool | LowAmbFanPrerun 60sec | 0 sec | through | 255 sec |  |  |  | the amount of time the indoor blower must operate before compressor operation is permitted when OprOAT is below LowAmb10On5OffSp
|  |  |  | LowAmb10On5OffSP | LowAmb10On5OffSp 45 F | 0 F | through | 60 F |  |  |  | if compressor operation otherwise is permitted, C# output cycled on 10 minutes/off 5 minutes with OprOAT below this setpoint
|  |  |  | LeadLag-En | LeadLag-En No | Yes | [5 empty] | effective for 2 or more compressor stages; Yes permits compressor equalized runtime where the C# output with the least C#RunTim operates first, the the C# output with the next least C#RunTim operates second, etc. No operates the C1 output first, the C2 output second, etc.
|  |  |  | Tstat-Only | Tstat-Only Yes | No | [5 empty] | Yes permits only thermostat inputs to initiate comfort control requests for heating, cooling and indoor blower operation; scheduling and comfort control by sensor inputs are disabled
|  |  |  | ClgOATCutout | ClgOATCutout 45 F | 0 F | through | 100 F |  |  |  | if ClgOATCutout-En = Yes, C# output is not permitted if OprOAT falls below this setpoint
|  |  | FDD | UnitType | UnitType Package Cool | [5 empty] | FDD board present
|  |  |  | EER | EER 11 | [5 empty] | FDD board present
|  |  |  | SubcoolGoal | SubcoolGoal 10 F | [5 empty] | FDD board present
|  |  |  | RefrigType | RefrigType R410A | [5 empty] | FDD board present
|  |  |  | HiSidePortLo | HiSidePortLo Discharge | [5 empty] | FDD board present
|  |  |  | EvapCoil-Type | EvapCoil-Type MicroChannel | [5 empty] | FDD board present
|  |  |  | CondCoil-Type | CondCoil-Type MicroChannel | [5 empty] | FDD board present
|  |  |  | InMeterDev-Type | InMeterDev-Type TxV | [5 empty] | FDD board present
|  |  |  | OutMeterDev-Type | OutMeterDev-Type n | [5 empty] | FDD board present
|  |  |  | UnitCap | UnitCap .0Ton | [5 empty] | FDD board present
|  |  |  | FanPower | FanPower .0kW | [5 empty] | FDD board present
|  |  |  | SuperHeatGoal | SuperHeatGoal 10.0 F | [5 empty] | FDD board present
|  |  |  | Altitude | Altitude .0 ft | [5 empty] | FDD board present
|  |  | Econ | Econ-MinPos | Econ-MinPos 10 % | 0% | through | 100% |  |  |  | economizer minimum position effective with occupied status, indoor blower operation and when OAT is above LowAmb-Sp
|  |  |  | LowSpeedFan-MinPos | LowSpeedFan-MinPos 25 % | 0% | through | 100% |  |  |  | effective if FanCtl-Type ≠ Single Speed; economizer damper minimum position when the UCB VFD output is at slowest setting
|  |  |  | ExFType | ExFType None | Non-Modulating | Modulating Damper | Variable Frequency Fan |  |  |  | power exhaust fan mode selection; None = no power exhaust fan installed, Non-Modulating = power exhaust fan on/off by economizer position, (Modulating Damper = power exhaust fan on/off by exhaust damper position, exhaust damper position by BLDG PRES input), (Variable Frequency Fan = power exhaust fan VFD speed control by BLDG PRES input)
|  |  | Misc | SZVAVEn | SZVAVEn Off | On |  |  |  |  | FanCtl-Type = Variable Speed | On enables single zone VAV control sequences; Off enabled traditional VAV control sequences
|  |  |  | CntrlType | CntrlType Constant Volume
|  |  |  | EquipType | EquipType RTU
|  |  |  | PmpOut-En | PmpOut-En Disable | Enable
Self Test | Start | Confirm?
| Pause | Confirm?
| Cancel | Confirm?
| Test Status | Test Status Off
| Reset | Confirm?
View Results | FanResult | FanResult Available
| C1Result | C1Result Available
| C2Result | C2Result Available
| C3Result | C3Result Available
| C4Result | C4Result Available
| H1Result | H1Result Available
| H2Result | H2Result Available
| H3Result | H3Result Available
| EconResult | EconResult Available
| ExhResult | ExhResult Available

## SE Thermistor Chart
SE Thermistor Sensor Temperature vs. Volts DC vs. Resistance
Note for Field usage: expect reading variances up to ±5% due to inherent accuracy tolerances of test instruments
Temperature | pin-to-pin | Resistance | Temperature | pin-to-pin | Resistance
°F | Volts DC | Ω | °F | Volts DC | Ω
?Unrel open circuit | 3.625 | infinite | 75 | 1.51 | 10501
|  |  | 80 | 1.41 | 9298
-40 | 3.41 | 330073 | 85 | 1.32 | 8250
-35 | 3.38 | 276915 | 90 | 1.23 | 7332
-30 | 3.34 | 232613 | 95 | 1.14 | 6530
-25 | 3.3 | 195716 | 100 | 1.06 | 5827
-20 | 3.25 | 164994 | 105 | 0.99 | 5209
-15 | 3.19 | 139404 | 110 | 0.91 | 4665
-10 | 3.13 | 118050 | 115 | 0.85 | 4184
-5 | 3.07 | 100260 | 120 | 0.78 | 3759
0 | 3 | 85398 | 125 | 0.73 | 3382
5 | 2.92 | 72950 | 130 | 0.67 | 3048
10 | 2.84 | 62495 | 135 | 0.62 | 2751
15 | 2.75 | 53685 | 140 | 0.57 | 2488
20 | 2.66 | 46240 | 145 | 0.53 | 2252
25 | 2.56 | 39929 | 150 | 0.49 | 2042
30 | 2.46 | 34565 | 155 | 0.45 | 1855
35 | 2.36 | 29998 | 160 | 0.42 | 1686
40 | 2.25 | 26099 | 165 | 0.39 | 1535
45 | 2.14 | 22763 | 170 | 0.36 | 1399
50 | 2.03 | 19900 | 175 | 0.33 | 1277
55 | 1.93 | 17435 | 180 | 0.31 | 1168
60 | 1.82 | 15309 | 185 | 0.29 | 1070
65 | 1.71 | 13472 | 190 | 0.27 | 980
70 | 1.61 | 11881 | ?Unrel short circuit | 0 | 0

## Color Legend
Conditional Parameter
Economizer Board Parameter
4-stage Board Parameter
FDD Master Board Parameter
FDD Slave Board Parameter
Selection and Economizer Board Parameter