## Split System
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point/ *Enum drop down list | Type | Modbus Point | Read/Write | Settting value/ *drop down list
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level |  | Set at board level |  | 4 to 127
|  | OccMode | Commission>HVACZone>OccMode | 29518 | MV | 82 | Read/Write | External/ Schedule
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | MV | 84 | Read/Write | Occupied/ Unoccupied
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | MV | Set at board level |  | "Yes" or "No" (Set to Yes for Split System Operation)
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level |  | Set at board level |  | *Modbus Field Bus
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | MV | Set at board level |  | OFF
|  | Alarms | Alarms |  |  |  |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level |  | Set at board level |  | defaulted to 1
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level |  | Set at board level |  | Auto or 1200-76800
|  | Unit Name | Details>Unit>Name | Set at board level |  | Set at board level
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level |  | View at Board level |  | Current Version 3.0.0.1072
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level |  | Set at board level |  | "TRUE" or "FALSE"
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | MV | 292 | Read | OCC/UNOCC
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | AV | 80 | Read/Write | ON/OFF
|  | Self Test | Self Test>Start | Set at board Level |  | Set at board level |  | *Start
|  | Time | Update>Time | Set at Board Level |  | Set at board level |  | 24 hours Military Format
|  | Unit Status | Status>Unit-S | *29803 | MV | 280 | Read
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>Split | Set at board level |  |  |  | *Split
COOLING SETUP/STATUS |  |  |  | (Note: # of Heating and Cooling Stages will have to be adjusted appropriately for Heat Pump Operation)
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | MV | 93 | Read/Write | ON
|  | Pump Out Enable | Details>Service>Factory>Misc>Pumpout-En | 29921 | MV |  | Read/Write | Used on J30YD, J40YD, J50YD models only
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | AV | 263 | Read | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | AV | Set at board level |  | 1 to 4 (Can't be less than 2 stages for Heat pump)
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | AV | 32 | Read/Write | 1 to 4 Circuits (Must equal number of Cooling Stages)
|  | Cooling Status | Status>Clg-S | *29577 | MV | 308 | Read | Displays Cooling Status
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | MV | 94 | Read/Write | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | AV | 21 | Read/Write | 0 to 100 degrees
|  | Low Ambient Enabled | Details>Control>Clg>Setup>LowAmb-En | 29928 | MV | Set at board level |  | "YES" or "NO"(Set to "NO" with Split System)
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | MV | Set at board level |  | "YES" or "NO"
|  | Constant Volume Occupied Cooling Setpoint | Details>Setpoints>ClgOcc-Sp | 29608 | AV | 29 | Read/Write | range 45 to 98 degrees
|  | Constant Volume Unoccupied Cooling Setpoint | Details>Setpoints>ClgUnocc-Sp | 29609 | AV | 30 | Read/Write | range 46 to 99 degress
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | MV | 98 | Read/Write | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | AV | 25 | Read/Write | 40 to 65 degrees
|  | Compressor 1 Command | Details>Control>Clg>Stage 1>C1-Cl | 29611 | MV | 311 | Read
|  | Compressor 1 Status | Details>Control>Clg>Stage1>C1-S | *29615 | MV | 312 | Read
|  | Compressor 1 Enabled | Details>Control>Clg>Stage1>C1-En | 29619 | MV | 101 | Read
|  | Compressor 1 Accumulated Run Time | Details>Control>Clg>Stage1>C1RunTim | 29627 | MV | 33 | Read/Write
|  | Compressor 2 Command | Details>Control>Clg>Stage2>C2-Cl | 29612 | MV | 319 | Read
|  | Compressor 2 Status | Details>Control>Clg>Stage2>C2-S | *29616 | MV | 320 | Read
|  | Compressor 2 enabled | Details>Control>Clg>Stage2>C2-En | 29620 | MV | 102 | Read
|  | Compressor 2 Accumulated Run time | Details>Control>Clg>Stage2>C2RunTim | 29628 | AV | 34 | Read/Write
|  | Compressor 3 Command | Details>Control>Clg>Stage3>C3-Cl | 29613 | MV | 327 | Read
|  | Compressor 3 Status | Details>Control>Clg>Stage3>C3-S | *29617 | MV | 328 | Read
|  | Compressor 3 Enabled | Details>Control>Clg>Stage3>C3-En | 29621 | MV | 103 | Read
|  | Compressor 3 Accumulated Run Time | Details>Control>Clg>Stage3>C3RunTim | 29629 | AV | 35 | Read/Write
|  | Compressor 4 Command | Details>Control>Clg>Stage4>C4-Cl | 29614 | MV | 335 | Read
|  | Compressor 4 Status | Details>Control>Clg>Stage4>C4-S | *29618 | MV | 336 | Read
|  | Compressor 4 Enabled | Details>Control>Clg>Stage4>C4-En | 29622 | MV | 104 | Read
|  | Compressor 4 Accumulated Run Time | Details>Control>Clg>Stage4>C4RunTim | 29630 | AV | 36 | Read/Write
HEAT PUMP |  | (Note: # of Heating and Cooling Stages will have to be adjusted appropriately for Heat Pump Operation)
|  | Heat Pump number of Stages | Details>Service>Factory>Standard>#HtPumpStgs | 29898 | AV | Set at board level |  | 1 to 2 stages
|  | Defrost Curve Set | Commission>Defrost>DefrostCurveSel | 29899 (Defrost State) | MV | 177 | Read/Write | Curve Selection 1 through 6
|  | Reversing Valve | Summary>HeatPump>RevVlv | 29900 |  | 366 | Read | Output Status
|  | Auxillary Heat | Summary>HeatPump>AuxHtg | 29901 |  | 367 | Read | Output Status
|  | Heat Pump Mode | Summary>HeatPump>Mode | 29902 |  | 368 | Read | Operating Status
HEATING SETUP/STATUS |  |  |  | (Note: # of Heating and Cooling Stages will have to be adjusted appropriately for Heat Pump Operation)
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | MV | 105 | Read/Write | "ON" if heat is used
|  | Heating Status | Status>Htg-S | *29708 | MV | 347 | Read
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | AV | 264 | Read | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | AV | Set at board level |  | 1 to 3
*29550
FAN_OFF_IDLE = 0
FAN_ON_PURGE = 1
FAN_ON_GAS_VALVE = 2
FAN_ON_DEFROST = 3
FAN_ON_THERMOSTAT_REQST = 4
FAN_ON_FAN_OFF_DELAY_COOL = 5
FAN_ON_FAN_OFF_DELAY_HEAT = 6
FAN_ON_CONTINUOUS_FAN_OCC_OP = 7
[9 empty] | FAN_ON_NORMAL_COMMAND = 8 | *Wired Field Bus = BACnet MSTP
[9 empty] | FAN_OFF_EXCEEDING_DUCT_PRESSURE = 9 | *N2 Slave Field Bus
[9 empty] | FAN_OFF_LOW_VOLTAGE = 10 | *Modbus Field Bus
FAN_OFF_FAN_OVERLOAD_LOCKOUT = 11
[9 empty] | FAN_OFF_FAN_VFD_FAULT = 12 | *Start
[9 empty] | FAN_OFF_HOT_WATER_FREEZE_STAT = 13 | *Pause
[9 empty] | FAN_OFF_AIR_PROVING_SWITCH = 14 | *Cancel
[9 empty] | FAN_OFF_MIN_OFF_DELAY = 15 | *Status
[9 empty] | FAN_OFF_FAN_ON_DELAY_HEAT = 16 | *Reset
FAN_OFF_FAN_ON_DELAY_COOL = 17
*Split
*RTU
[9 empty] | *29577 | *Heat Pump
[9 empty] | COOL_OFF_IDLE = 0 | *Unknown
COOL_THERM_COOLING = 1
[9 empty] | COOL_UNOCC_COOLING = 2 | * Auto
[9 empty] | COOL_OCC_COOLING = 3 | * Dry Bulb
[9 empty] | COOL_OFF_OAT_LOCKOUT = 4 | * Single Enthalpy
[9 empty] | COOL_OFF_DISABLED = 5 | * Dual Enthalpy
COOL_OFF_LOCKOUT= 6
[9 empty] | COOL_OFF_LOW_SUPPLY_VOLT = 7 | *None
[9 empty] | COOL_OFF_LOW_AMBIENT = 8 | *Non-Modulating
[9 empty] | COOL_OFF_LOW_AMBIENT_PRE_RUN_DELAY = 9 | *Modulating Damper
[9 empty] | COOL_OFF_WAITING_CHANGEOVER 10 | *Variable Frequency Fan
COOL_OFF_FREE_COOLING 11
[9 empty] | COOL_COMFORT_VENT 12 | *Off-Idle
*On-Normal Command
[9 empty] | *29615 | *Off-Disabled
[9 empty] | CLG_1_OFF_IDLE = 0 | *Off-VFD Fault
[9 empty] | CLG_1_ON_MIN_ON_TIME = 1 | *Off-Low Building Static Pressure
[9 empty] | CLG_1_ON_NORMAL_CMD = 2 | *Off-Economizer Damper Position
CLG_1_OFF_CLG_DISABLED = 3
[9 empty] | CLG_1_OFF_OAT_CUTOUT = 4 | *Disabled
[9 empty] | CLG_1_OFF_LOW_AMBIENT_TEMP = 5 | *Controlled by IAQ
[9 empty] | CLG_1_OFF_LOW_SUPPLY_VOLT = 6 | *Diff. Between IAQ & OAQ
CLG_1_OFF_HIGH_PRESSURE_LOCK = 7
[9 empty] | CLG_1_OFF_LOW_PRESSURE_LOCK = 8 | *Unreliable
[9 empty] | CLG_1_OFF_FREEZE_CONDITION = 9 | *Return Air Temp
[9 empty] | CLG_1_OFF_ANTI_SHORT_CYCLE_DELAY = 10 | *Local Input
[9 empty] | CLG_1_OFF_COOLING_STAGE_DISABLED = 11 | *Network Sensor
*BAS Override
[9 empty] | *29616 | *Not Available
CLG_2_OFF_IDLE = 0
CLG_2_ON_MIN_ON_TIME = 1
CLG_2_ON_NORMAL_CMD = 2
CLG_2_OFF_CLG_DISABLED = 3
CLG_2_OFF_OAT_CUTOUT = 4
CLG_2_OFF_LOW_AMBIENT_TEMP = 5
CLG_2_OFF_LOW_SUPPLY_VOLT = 6
CLG_2_OFF_HIGH_PRESSURE_LOCK = 7
CLG_2_OFF_LOW_PRESSURE_LOCK = 8
CLG_2_OFF_FREEZE_CONDITION = 9
CLG_2_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_2_OFF_COOLING_STAGE_DISABLED = 11
*29617
CLG_3_OFF_IDLE = 0
CLG_3_ON_MIN_ON_TIME = 1
CLG_3_ON_NORMAL_CMD = 2
CLG_3_OFF_CLG_DISABLED = 3
CLG_3_OFF_OAT_CUTOUT = 4
CLG_3_OFF_LOW_AMBIENT_TEMP = 5
CLG_3_OFF_LOW_SUPPLY_VOLT = 6
CLG_3_OFF_HIGH_PRESSURE_LOCK = 7
CLG_3_OFF_LOW_PRESSURE_LOCK = 8
CLG_3_OFF_FREEZE_CONDITION 9
CLG_3_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_3_OFF_COOLING_STAGE_DISABLED = 11
*29618
CLG_4_OFF_IDLE = 0
CLG_4_ON_MIN_ON_TIME = 1
CLG_4_ON_NORMAL_CMD = 2
CLG_4_OFF_CLG_DISABLED = 3
CLG_4_OFF_OAT_CUTOUT = 4
CLG_4_OFF_LOW_AMBIENT_TEMP = 5
CLG_4_OFF_LOW_SUPPLY_VOLT = 6
CLG_4_OFF_HIGH_PRESSURE_LOCK = 7
CLG_4_OFF_LOW_PRESSURE_LOCK = 8
CLG_4_OFF_FREEZE_CONDITION = 9
CLG_4_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_4_OFF_COOLING_STAGE_DISABLED = 11
*29803
UNIT_IDLE = 0
UNIT_SD_ALARM = 1
UNIT_PURGE_COMMAND = 2
UNIT_SELF_TEST = 3
UNIT_MORNING_WARM_UP= 4
UNIT_AIR_TEMPERING = 5
UNIT_DEHUMIDIFICATION = 6
UNIT_HEATING = 7
UNIT_COOLING = 8
UNIT_ECONOMIZER = 9
UNIT_FAN_ONLY = 10
UNIT_COMFORT_VENTILATION = 11
*29708
HEAT_OFF_IDLE = 0
HEAT_ON_DEFROST = 1
HEAT_SAT_TEMPERING = 2
HEAT_MORNING_WARMUP = 3
HEAT_TSTAT_HEATING = 4
HEAT_UNOCC_HEATING = 5
HEAT_OCC_HEATING = 6
HEAT_OFF_DISABLED = 7
HEAT_OFF_OAT_LOCKOUT = 8
HEAT_OFF_SAT_LIMIT = 9
HEAT_OFF_WAITING_FOR_CHANGEOVER = 10
HEAT_COMFORT_VENTILATION = 11
*29750
ECONOMIZER_DISABLED = 0
ECONOMIZER_DAMPER_NOT_FUNCTIONAL = 1
ECONOMIZER_PURGE = 2
ECONOMIZER_UNAVAIL_SENSOR_FAULT = 3
ECONOMIZER_ECON_LOADING = 4
ECONOMIZER_SAT_HIGH_LIMIT = 5
ECONOMIZER_MIXED_AIR_LL = 6
ECONOMIZER_DEMAND_VENT_AIR_QUALITY = 7
ECONOMIZER_OUTDOOR_AIRFLOW_CNTL = 8
ECONOMIZER_FREE_CLG_IS_AVAIL = 9
ECONOMIZER_MIN_POSITION = 10
ECONOMIZER_TEST = 11
ECONOMIZER_COMFORT_VENTILATION = 12
ECONOMIZER_LOW_OA_AMBIENT = 13
*29777
EXHAUST_FAN_OFF_IDLE = 0
EXHAUST_FAN_ON_NORMAL_COMMAND = 1
EXHAUST_FAN_OFF_DISABLED = 2
EXHAUST_FAN_OFF_VFD_FAULT = 3
EXHAUST_FAN_OFF_LOW_BLDG_STATIC_PRESSURE = 4
EXHAUST_FAN_OFF_ECON_DAMPTER_POS = 5
*29791
HOT_GAS_OFF_IDLE = 0
HOT_GAS_ON_NORMAL_COMMAND = 1
HOT_GAS_ON_ALT_OPERATION_CMD = 2
HOT_GAS_OFF_DISABLED = 3
*29735
Htg_1_OFF_IDLE = 0
Htg_1_ON_DEFROST = 1
Htg_1_SAT_TEMPERING = 2
Htg_1_MORNING_WARMUP = 3
Htg_1_TSTAT_HEATING = 4
Htg_1_UNOCC_HEATING = 5
Htg_1_OCC_HEATING = 6
Htg_1_OFF_DISABLED = 7
Htg_1_OFF_OAT_LOCKOUT = 8
Htg_1_OFF_SAT_LIMIT = 9
Htg_1_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_1_COMFORT_VENTILATION = 11
*29736
Htg_2_OFF_IDLE = 0
Htg_2_ON_DEFROST = 1
Htg_2_SAT_TEMPERING = 2
Htg_2_MORNING_WARMUP = 3
Htg_2_TSTAT_HEATING = 4
Htg_2_UNOCC_HEATING = 5
Htg_2_OCC_HEATING = 6
Htg_2_OFF_DISABLED = 7
Htg_2_OFF_OAT_LOCKOUT = 8
Htg_2_OFF_SAT_LIMIT = 9
Htg_2_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_2_COMFORT_VENTILATION = 11
*29737
Htg_3_OFF_IDLE = 0
Htg_3_ON_DEFROST = 1
Htg_3_SAT_TEMPERING = 2
Htg_3_MORNING_WARMUP = 3
Htg_3_TSTAT_HEATING = 4
Htg_3_UNOCC_HEATING = 5
Htg_3_OCC_HEATING = 6
Htg_3_OFF_DISABLED = 7
Htg_3_OFF_OAT_LOCKOUT = 8
Htg_3_OFF_SAT_LIMIT = 9
Htg_3_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_3_COMFORT_VENTILATION = 11
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool.
Note on B5: cedmonja: This point will occupy and unoccupy the unit through bacnet.
Note on B6: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B7: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B8: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B10: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B14: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B15: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B16: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B17: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B24: Chad Edmondson: The "Pump Out On Start Up" function is a standard feature on the 30-50 ton matched split systems. The dual circuit indoor evaporator refrigerant circuits include two TXV's with normally closed solenoid valves that are utilized for the "Pump Out On Start Up" sequence of operation. The pump out sequence is designed to prevent liquid refrigerant flooding of the compressors during startup. The pump out circuit is activated each time the first and third stage compressors (Y1, Y3) are called for from the thermostat. The pump out circuitry does not allow the POS (pump out solenoid) located in the liquid line just ahead of the TXVs to open, thus not allowing refrigerant flow, or liquid refrigerant to enter the scroll compressor during startup. The pump out solenoid remains closed and not allowing refrigerant flow through the system until the active refrigerant circuit's low pressure switch opens. Once the low pressure switch opens PS relay 1 or 2 opens the POS (Pump Out Solenoid) and allows refrigerant to begin flowing through the active refrigerant circuit. The active systems low pressure switch (LPS) is ignored for approximately 1 minute while the systems suction pressure rises above the LPS cutout point of 71 psi.
Note on B26: Chad Edmondson: When RTU is a Heat pump or Series 40 the minimum stage setting is 2.
Note on B27: Chad Edmondson: #1 of circuits are set to 1 when used with a series 40 condensing unit. This will allow proper operation of high and low pressure switches.
Note on B29: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B30: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B31: cedmonja: If Cooling OAT Cutout Enble is Yes, the compressor is not permitted if the OAT is less than the cooling OAT Cutout. If Cooling OAT Cutout Enable is NO. the compressor cycles 10 minutes On and 5 minutes Off if the OAT is less than the LowAmb10On5Off Setpoint. If a compressor is in the 10 min On cycle and the evaportator temperature (EC1 thru EC4) drops below 26 degrees F. the compressor output de-endergizes and the 5 minute ASCD starts. After 5 minutes ASCD expires, the compressor ouput is permitted. Anytime the compressor output de-energizes due to the evaporator coil temperature protection it does not count towards a hard compressor lockout.
Note on B32: Chad Edmondson: Split system operation set to 'NO". If set to "YES" improper condenser fan motor operation will occur and unit will trip on high head pressure.
Note on B35: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B55: cedmonja: The number of heat pump stages; 1 or more enabled the UCB H1 VAC output to position reversing valve, 2 ormore enabled the UCB H2 VAC output to initiate supplemental heat.
Note on B59: cedmonja: Cooling: Cooling calls are handled the same way as non-heat pump cooling units with one exception. Exception: During cooling, the control energizes the H1 output to turn on the Reversing Valve. The H1 output to the reversing valve remains energized between calls for cooling. If a heating call arises, the H1 output turns off. Heating: If a first stage of heating is called for (thermostat or zone sensor/network), all available compressors stage on, with a 30 second time delay between compressors. The Cooling Fan On Delay and Cooling Fan Off Delay are used for the first stage of heat pump heating. During a first stage of heating, the H1 output turns off and remain off between heat calls. If a second stage of heating is called for, the H2 or AUX output energizes the Emergency/Aux heating. If a thermostat calls for W2 only, only the H2 output energizes. The Heating Fan On Delay and Heating Fan Off Delay are used.

## RTU-SingleSpeed
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point/ *Enum drop down list | Type | Modbus Point | Read/Write | Settting value/ *drop down list
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level |  | Set at board level |  | 4 to 127
|  | OccMode | Commission>HVACZone>OccMode | 29518 | MV | 82 | Read/Write | External/ Schedule
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | MV | 84 | Read/Write | Occupied/ Unoccupied
|  | Occupancy Binary Input | Details>Service>Inputs>BinaryInputs>Occ | 29516 | MV | 291 | Read | Occupied/ Unoccupied
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | MV | Set at board level |  | "Yes" or "No"
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level |  | Set at board level |  | *Modbus Field Bus
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | MV | Set at board level |  | OFF/ ON
|  | Alarms | Alarms |  |  |  |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level |  | Set at board level |  | defaulted to 1
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level |  | Set at board level |  | Auto or 1200-76800
|  | Unit Name | Details>Unit>Name | Set at board level |  | Set at board level |  |  | Cooling Adaptive Tuning Default Parameters- Not Adjustable
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level |  | View at Board level |  | Current Version 3.0.0.1072 | Default Tuning Parameters
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level |  | Set at board level |  | "TRUE" or "FALSE" |  | Initial Prop Band | Intergral Time (sec)
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | MV | 292 | Read | Occupied/ Unoccupied | Zone- T | 4.2 | 892
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | AV | 80 | Read/Write | ON/OFF | DA-T | 21.8 | 203
|  | Self Test | Self Test>Start | Set at board Level |  | Set at board level |  | *Start
|  | Cooling Adaptive Tuning Enabled | Details>Control>Clg>Setup>ClgAdapTunEn | 29882 | MV | 100 | Read/Write | "Yes" or "No"
|  | Heating Adaptive Tuning Enabled | Details>Control>Htg>Setup>HtgAdapTunEn | 29881 | MV | 114 | Read/Write | "Yes" or "No"
|  | Time | Update>Time | Set at Board Level |  | Set at board level |  | 24 hours Military Format
|  | Unit Status | Status>Unit-S | *29803 | MV | 280 | Read
|  | Off During Unoccuped Mode | Commision>HVACzone>OffDurUnocc | 29914 | MV | 88 | Read/Write | "Yes" or "No"
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>RTU | Set at board level |  |  |  | *RTU
|  | Bacnet Encoding Type | Controller>Network>EncodingType | *32578 | MV |  |  | 3.0.0.1116 Rev or higher
|  | Temporary Occupancy Timeout | Details>Zone>Indoor>TempOccTimeout | 29521 | AV | 85 | Read/Write | 30 to 120 min. time period
FAN SETUP/STATUS
|  | Fan Control | Summary>Fan>FanCtl-Type | 29555 | MV | Set at board level |  | Single Speed 100% fan operation
|  | APS Setup | Details>Service>Factory>Standard>APS Setup | 29556 | MV | Set at board level |  | None or Constant
|  | APS Status | Details>Control>IndoorFan>Status>APS | 29557 | MV | 305 | Read | ON = APS closed
|  | Net Override Fan Request | Details>Service>Inputs>NetworkInputs>NetFanReq | 29536 | MV | 87 | Read/Write | OFF / ON
|  | Fan "OFF" Delay Cool | Details>Control>IndoorFan>Setup.FanOffDlyCool | 29559 | AV | Set at board level |  | 0 to 255 second timer
|  | Fan "OFF" Delay Heat | Details>Control>IndoorFan>Setup>FanOffDlyHeat | 29561 | AV | Set at board level |  | 0 to 255 second timer
|  | Fan "OFF" Start Heat | Details>Control>IndoorFan>Setup>FanoffStartHeat | 29569 | MV | 92 | Read/Write | "YES" or "NO"
|  | Fan "ON" Delay Cool | Details>Control>IndoorFan>Setup>FanOnDlyCool | 29558 | AV | 90 | Read/Write | 0 to 30 second timer
|  | Fan "ON" Delay Heat | Details>Control>IndoorFan>Setup>FanOnDlyHeat | 29560 | AV | Set at board level |  | 0 to 30 second timer
|  | Fan "ON" Occupied | Details>Control>IndoorFan>Setup>FanOnOcc | 29568 | MV | 91 | Read/Write | "YES" or "NO"
|  | Fan Overload | Details>Control>IndoorFan>Setup>FanOvrload | 29553 | MV | 304 | Read
|  | Fan Status | Status>Fan-S | *29550 | MV | 302 | Read
COOLING SETUP/STATUS
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | MV | 93 | Read/Write | "Yes" or "No"
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | AV | 263 | Read | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | AV | Set at board level |  | 1 to 4
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | AV | 32 | Read/Write | 1 to 4 Circuits
|  | Cooling Status | Status>Clg-S | *29577 | MV | 308 | Read | Displays Cooling Status
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | MV | 94 | Read/Write | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | AV | 21 | Read/Write | 0 to 100 degrees
|  | Low Ambient Enabled | Details>Control>Clg>Setup>LowAmb-En | 29928 | MV | Set at board level |  | "YES" or "NO"
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | MV | Set at board level |  | "YES" or "NO"
|  | Constant Volume Occupied Cooling Setpoint | Details>Setpoints>ClgOcc-Sp | 29608 | AV | 29 | Read/Write | range 45 to 98 degrees
|  | Constant Volume Unoccupied Cooling Setpoint | Details>Setpoints>ClgUnocc-Sp | 29609 | AV | 30 | Read/Write | range 46 to 99 degress
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | MV | 98 | Read/Write | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | AV | 25 | Read/Write | 40 to 65 degrees
|  | Compressor 1 Command | Details>Control>Clg>Stage 1>C1-Cl | 29611 | MV | 311 | Read
|  | Compressor 1 Status | Details>Control>Clg>Stage1>C1-S | *29615 | MV | 312 | Read
|  | Compressor 1 Enabled | Details>Control>Clg>Stage1>C1-En | 29619 | MV | 101 | Read
|  | Compressor 1 Accumulated Run Time | Details>Control>Clg>Stage1>C1RunTim | 29627 | MV | 33 | Read/Write
|  | Compressor 2 Command | Details>Control>Clg>Stage2>C2-Cl | 29612 | MV | 319 | Read
|  | Compressor 2 Status | Details>Control>Clg>Stage2>C2-S | *29616 | MV | 320 | Read
|  | Compressor 2 enabled | Details>Control>Clg>Stage2>C2-En | 29620 | MV | 102 | Read
|  | Compressor 2 Accumulated Run time | Details>Control>Clg>Stage2>C2RunTim | 29628 | AV | 34 | Read/Write
|  | Compressor 3 Command | Details>Control>Clg>Stage3>C3-Cl | 29613 | MV | 327 | Read
|  | Compressor 3 Status | Details>Control>Clg>Stage3>C3-S | *29617 | MV | 328 | Read
|  | Compressor 3 Enabled | Details>Control>Clg>Stage3>C3-En | 29621 | MV | 103 | Read
|  | Compressor 3 Accumulated Run Time | Details>Control>Clg>Stage3>C3RunTim | 29629 | AV | 35 | Read/Write
|  | Compressor 4 Command | Details>Control>Clg>Stage4>C4-Cl | 29614 | MV | 335 | Read
|  | Compressor 4 Status | Details>Control>Clg>Stage4>C4-S | *29618 | MV | 336 | Read
|  | Compressor 4 Enabled | Details>Control>Clg>Stage4>C4-En | 29622 | MV | 104 | Read
|  | Compressor 4 Accumulated Run Time | Details>Control>Clg>Stage4>C4RunTim | 29630 | AV | 36 | Read/Write
HEATING SETUP/STATUS
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | MV | 105 | Read/Write | "YES" or "NO"
|  | Heating Status | Status>Htg-S | *29708 | MV | 347 | Read
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | AV | 264 | Read | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | AV | Set at board level |  | 1 to 3
|  | Constant Volume Occupied Heating Setpoint | Details>Setpoints>CVHtgOcc-Sp | 29728 | AV | 42 | Read/Write | Range 46 to 99 degrees
|  | Constant Volume Unoccuped Heating Setpoint | Details>Setpoints>CVHtgUnocc-Sp | 29729 | AV | 43 | Read/Write | Range 45 to 98 degrees
|  | Heating OAT Cutout Setpoint | Details>Control>Htg>Setup>HtgOATCutout-Sp | 29711 | AV | 38 | Read/Write | 0 to 100 degrees
|  | Heating Stage 1 Command | Details>Control>Htg>Stage1>H1 | 29732 | MV | 359 | Read
|  | Heating Stage 1 Status | Details>Cotrol>Htg>Stage1>H1-S | *29735 | MV | 360 | Read
|  | Heating Stage 2 Command | Details>Control>Htg>Stage2>H2 | 29733 | MV | 361 | Read
|  | Heating Stage 2 Status | Details>Cotrol>Htg>Stage2>H2-S | *29736 | MV | 362 | Read
|  | Heating Stage 3 Command | Details>Control>Htg>Stage3>H3 | 29734 | MV | 363 | Read
|  | Heating Stage 3 Status | Details>Cotrol>Htg>Stage3>H3-S | *29737 | MV | 364 | Read
|  | Supply Air Heating Limit Enabled | Detals>Control>Htg>Setup>SATHtgLimit-En | 29709 | MV | 106 | Read/Write | "YES" or "NO"
|  | Supply Air Heating Limit Set point | Details>Control>Htg>Setup>SATHtgLimt-Sp | 29710 | AV | 37 | Read/Write | 100 degree to 180 degrees
|  | Hot Water Heat Valve % Output (4 stage Exp Board) | Details>Control>Htg>Status>HWV | 29741 | AV | 252 | Read | 0 to 100%
|  | Hot Water Valve Rev Acting (4 stage Exp. Board) | Details>Control>Htg>Setup>HydReverse | 29742 | MV | 115 | Read/Write | "YES" or "NO"
|  | Hot Water Htg Stage 1 SAT Sp (4 stage Exp. Board) | Details>Control>Htg>Setup>HydH1SA-Sp | 29743 | AV | 51 | Read/Write | 80 to 180 degrees
|  | Hot Water Htg Stage 2 SAT Sp ( 4 stage Exp. Board) | Details>Control>Htg>Setup>HydH2SA-Sp | 29744 | AV | 52 | Read/Write | 80 to 180 degrees
|  | Hot Water Heat SAT Tempering Enabled (4 stage Exp. Board) | Details>Control>Htg>SATTempHydHt-En | 29745 | MV | 116 | Read/Write | "Yes" or "No"
|  | Hot Water Heat SAT Tempering Set Point (4 stage Exp. Board) | Commission>Htg>SATTempHydHt-Sp | 29746 | AV | 53 | Read/Write
|  | Hot Water Freeze Stat (4 stage Exp. Board) | Details>Service>Inputs>BinaryInputs>Limit>FSHW | 29712 | MV | 348 | Read | Normal or Alarm
|  | Heating Control Type | Details>Control>Htg>Status>Htg-Type | Set at board Level |  | Set at board level |  | Staged or Proportional
ECONOMIZER SETUP/STATUS
|  | Economizer Enabled | Commission>Econ>Econ-En | 29747 | MV | 118 | Read/Write | "YES" or "NO"
|  | Economizer Status | Status>Econ-S | *29750 | MV | 370 | Read
|  | Economizer Firware | Controller>SysCntrls>Econ>EconMainVer | N/A |  | N/A |  | View at board level or Map Gateway
|  | Economizer Damper Position | Details>Service>Inputs>Sensors>EconDampPos | 29748 | AV | 253 | Read | % open
|  | Economizer Minimum Position | Details>Control>Econ>Setup>Econ-MinPos | 29759 | AV | 77 | Read/Write | % Open Set point
|  | Economizer OAT Set point | Details>Control>Econ>Setup>EconOAT-SpEn | 29753 | AV | 55 | Read/Write | 40 to 80 degrees
|  | Economizer Free Cooling Available | Summary>Econ>Econ-Free | 29749 | MV | 369 | Read | "YES" or "NO"
|  | Economizer Mechanical Setup | Details>Control>Econ>Setup>EconMechStp | 29912 | MV | Set at board level |  | Option B
|  | All Compressor OFF-Economizer | Details>Control>Clg>Setup>AllCompOff-Econ | 29584 | MV | 96 | Read/Write | "YES" or "NO"
|  | Econ OA Enthalpy Setpoint | Details>Control>Econ>Setup>EconOAEth-Sp | 29754 | AV | 56 | Read/Write | 10 to 50 BTU/Lb
|  | Free Cooling Selection | Details>Control>Econ>Setup>FreeClg-Sel | 29752 | MV | 119 | Read/Write | * Auto
|  | VAV Clg SA Upper Stpt | Details>Setpoints>SATUp-Sp | 29604 | AV | 26 | Read/Write | 60 degree (Use for Econ. Mech Option B)
|  | VAV Clg SA Lower Stpt | Details>Setpoints>SATLo-Sp | 29605 | AV | 27 | Read/Write | 55 degree (Use for Econ. Mech Option B)
|  | Economizer Loading Enabled | Details>Control>Clg>Setup>EconLoad-En | 29583 | MV | 95 | Read/Write | "YES" or "NO"
|  | Economzer Fault Detection Enable | Commission>Econ>EconFltDetectEn | 29915 | MV | 132 | Read/Write | Disable/Enable
POWER EXHAUST SETUP/STATUS
|  | Power Exhaust Fan Type | Details>Service>Factory>Econ>ExFType | 29774 |  | set at board level |  | *None
|  | Power Exhaust Fan Command | Details>Control>PowerEx>Status> | 29775 | MV | 376 | Read
|  | Power Exhaust Fan Status | Details>Control>PowerEx>Status>ExFan | *29777 | MV | 377 | Read | *Off-Idle
|  | Power Exhaust Modulating Damper Output | Summary>PowerEx>EAD-O | 29782 | AV | 261 | Read
|  | Building Pressure Set Point | Summary>PowerEx>Bldg-Sp | 29780 | AV | 63 | Read/Write
|  | Econ Damper Position Power Exhaust "OFF" | Summary>PowerEx>EconDmpPosFanOff | 29786 | AV | 67 | Read/Write
|  | Econ Damper Position Power Exhaust "ON" | Summary>PowerEx>EconDmpPosFanOn | 29785 | AV | 66 | Read/Write
|  | Power Exhaust Damper Position "OFF" | Commission>PoweEx>ExDmpPosFanOff | 29784 | AV | 65 | Read/Write
|  | Power Exhaust Damper Position "On" | Commission>PoweEx>ExDmpPosFanOn | 29783 | AV | 64 | Read/Write
|  | Power Exhaust VFD Output Status | Summary>PowerEx>ExFanVFD | 29776 | AV | 258 | Read
CO2 DEMAND VENTILATION SETUP/STATUS
|  | (CO2) Demand Ventilation Mode | Commission>Dvent>Dvent-Mode | 29765 | MV | 120 | Read/Write | *Disabled
|  | (CO2) Demand Ventilation Mode IAQ Set Point | Commission>Dvent>DventIAQ-Sp | 29767 | AV | 61 | Read/Write | 0 to 5000 ppm
|  | (CO2) Demand Ventilation Max Econ Damper Position | Commission>Dvent>DVentMaxEconPos | 29766 | AV | 60 | Read/Write | range 0% to 100% open
|  | (CO2) OAQ Range | Commission>Dvent>OAQRange | 29548 | MV | 301 | Read | 0 ppm to 5000 ppm
|  | (CO2) IAQ Range | Commission>Dvent>IAQRange | 29529 | AV | 294 | Read | 0 ppm to 5000 ppm
|  | (CO2) Demand Ventilation Differential Set Point | Commission>Dvent>DVentDiff-Sp | 29768 | AV | 62 | Read/Write | 0 ppm to 5000 ppm
SENSOR INPUTS & READINGS
|  | Supply Air Temperature | Details>Service>Inputs>Sensors>SAT | 29564 | AV | 158 | Read
|  | Return Air Temperature | Details>Service>Inputs>Sensors>RAT | 29764 | AV | 139 | Read
|  | Operational Outdoor Air Temperature | Details>Zone>Outdoor>OprOAT | 29541 | AV | 153 | Read
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29730 | AV | 251 | Read
|  | Constant Volume Operating Cooling Setpoint | Details>Setpoints>OprCVClg-Sp | 29610 | AV | 161 | Read
|  | Operational Space Temperature | Details>Zone>Indoor>OprST | 29522 | AV | 135 | Read
|  | Operational Space Sensor Offset | Details>Zone>Indoor>OprSSO | 29537 | AV | 140 | Read
|  | Space Temperature Source | Details>Zone>Indoor>STsrc | 29523 | MV | 293 | Read | *Return Air Temp
|  | Space Sensor Offset Range | Details>Zone>Indoor>SSORange | N/A |  | N/A |  | 0 to 5 degrees F setpoint
|  | Space sensor Offset Source | Details>zone>Indoor>SSOSrc | 29538 | MV | 298 | Read
|  | Space Humidity RAH input | Details>Control>Econ>Status>RAH | 29828 | AV | 138 | Read
|  | Outdoor Air Humidity Input | Details>Service>Inputs>Sensor>OAH | N/A
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OA-Enth | 29545 | AV | 155 | Read
|  | Return Air Enthalpy | Details>Control>Econ>Status>RA-Enth | 29763 | AV | 257 | Read
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531 | AV | 137 | Read
|  | Operational Outdoor Air Humidity | Details>Control>Econ>Status>OprOAH | 29544 | AV | 154 | Read
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OAH-Enth | 29545 | AV | 155 | Read
|  | Net Override Space Temperature | Details>Service>Inputs>NetworkInputs>NetST | 29526 | AV | 1 | Read/Write | Writable Point to Space Temp
|  | Net Override Outdoor Air Temperature | Details>Service>Inputs>NetworkInputs>NetOAT | 29543 | AV | 6 | Read/Write | Writable Point to OAT
|  | Net Override Indoor Air Quality | Details>Service>Inputs>NetworkInputs>NetIAQ | 29530 | AV | 3 | Read/Write | Writable Point to IAQ
|  | Net Override Outdoor Air Quality | Details>Service>Inputs>NetworkInputs>NetOAQ | 29549 | AV | 8 | Read/Write | Writable Point to OAQ
|  | Net Override Outdoor Air Humidity | Details>Service>Inputs>NetworkInputs>NetOAH | 29546 | AV | 7 | Read/Write | Writable Point to OAH
|  | Net Override Space Humidity | Details>Service>Inputs>NetworkInputs>NetSH | 29533 | AV | 4 | Read/Write | Writable Point to Space Humidity
|  | Net Override Space Sensor Offset | Details>Service>Inputs>NetworkInputs>NetSSO | 29540 | AV | 5 | Read/Write | Writable Point to Space Sensor offset
|  | Building Pressure | Summary>PowerEx>BldgPres | 29781 | AV | 260 | Read | (-).25 to .25"wc
|  | (CO2) IAQ Input | Details>Service>Inputs>Sensor>IAQ | N/A |  | N/A
|  | (CO2) OAQ Input | Details>Service>Inputs>Sensor>OAQ | N/A |  | N/A
|  | Operational IAQ | Summary>Dvent>OprIAQ | 29527 | AV | 136 | Read
|  | IAQ source | Details>Zone>Indoor>IAQsrc | 29528 | MV | 294 | Read
|  | Operational OAQ | Summary>Dvent>OprOAQ | 29547 | AV | 156 | Read
|  | OAQ source | Deatails>Zone>Outdoor>OAQsrc | 29548 | MV | 301 | Read
AIR MONITOR
|  | Fresh Air Enable | Details>Control>AirMonStation>FRSHAIR-EN | Set at board Level |  | Set at board level |  | Enable/Disable
|  | Fresh Air Flow Reading | Details>Control>AirMonStation>FR-Air | 29796 | AV | 262 | Read | CFM reading
|  | Air Monitor Flow Range | Details>Control>AirMonStation>MOA-Range | 29797 | AV | 70 | Read/Write | Range 0 to 50000 CFM
|  | Air Monitor Flow Setpoint | Details>Control>AirMonStation>MOAflow-Sp | 29795 | AV | 69 | Read/Write | Range 0 to 50000 CFM
HOT GAS REHEAT
|  | Hot Gas Reheat Enabled for Operation | Details>Service>Factory>Standard>HGR-En | 29789 | MV | 123 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Alternate Operation Enabled | Details>Control>HGR>HGRAlt-En | 29793 | MV | 124 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Gas Reheat Humidity Setpoint | Details>Control>HGR>HGRHum-SP | 29792 | AV | 68 | Read/Write | 0% to 100%
|  | Hot Gas Reheat Alternate Operation Writable | Details>Control>HGR>HGRAltWrite | 29794 |  | N/A | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Enabled for Unoccupied Operation | Details>Control>HGR>HGRUnocc-En | 29904 | MV | 133 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Unoccupied Humidity Setpoint | Details>Control>HGR>HGRUnoccHum-Sp | 29903 | AV | 78 | Read/Write | 0% to 100%
|  | Hot Gas Reheat Status | Details>Control>HGR>HGR-S | *29791 | MV | 380 | Read
HEAT PUMP |  | (Note: # of Heating and Cooling Stages will have to be adjusted appropriately for Heat Pump Operation)
|  | Heat Pump number of Stages | Details>Service>Factory>Standard>#HtPumpStgs | 29898 | AV | Set at board level |  | 1 to 2 stages
|  | Defrost Curve Set | Commission>Defrost>DefrostCurveSel | 29899 (Defrost State) | MV | 177 | Read/Write | Curve Selection 1 through 6
|  | Reversing Valve | Summary>HeatPump>RevVlv | 29900 |  | 366 | Read | Output Status
|  | Auxillary Heat | Summary>HeatPump>AuxHtg | 29901 |  | 367 | Read | Output Status
|  | Heat Pump Mode | Summary>HeatPump>Mode | 29902 |  | 368 | Read | Operating Status
[12 empty] | *29550 | *Wired Field Bus = BACnet MSTP
[12 empty] | FAN_OFF_IDLE = 0 | *N2 Slave Field Bus
[12 empty] | FAN_ON_PURGE = 1 | *Modbus Field Bus
FAN_ON_GAS_VALVE = 2
[12 empty] | FAN_ON_DEFROST = 3 | *Start
[12 empty] | FAN_ON_THERMOSTAT_REQST = 4 | *Pause
[12 empty] | FAN_ON_FAN_OFF_DELAY_COOL = 5 | *Cancel
[12 empty] | FAN_ON_FAN_OFF_DELAY_HEAT = 6 | *Status
[12 empty] | FAN_ON_CONTINUOUS_FAN_OCC_OP = 7 | *Reset
FAN_ON_NORMAL_COMMAND = 8
[12 empty] | FAN_OFF_EXCEEDING_DUCT_PRESSURE = 9 | *Split
[12 empty] | FAN_OFF_LOW_VOLTAGE = 10 | *RTU
[12 empty] | FAN_OFF_FAN_OVERLOAD_LOCKOUT = 11 | *Heat Pump
[12 empty] | FAN_OFF_FAN_VFD_FAULT = 12 | *Unknown
FAN_OFF_HOT_WATER_FREEZE_STAT = 13
[12 empty] | FAN_OFF_AIR_PROVING_SWITCH = 14 | * Auto
[12 empty] | FAN_OFF_MIN_OFF_DELAY = 15 | * Dry Bulb
[12 empty] | FAN_OFF_FAN_ON_DELAY_HEAT = 16 | * Single Enthalpy
[12 empty] | FAN_OFF_FAN_ON_DELAY_COOL = 17 | * Dual Enthalpy
*None
[12 empty] | *29577 | *Non-Modulating
[12 empty] | COOL_OFF_IDLE = 0 | *Modulating Damper
[12 empty] | COOL_THERM_COOLING = 1 | *Variable Frequency Fan
COOL_UNOCC_COOLING = 2
[12 empty] | COOL_OCC_COOLING = 3 | *Off-Idle
[12 empty] | COOL_OFF_OAT_LOCKOUT = 4 | *On-Normal Command
[12 empty] | COOL_OFF_DISABLED = 5 | *Off-Disabled
[12 empty] | COOL_OFF_LOCKOUT= 6 | *Off-VFD Fault
[12 empty] | COOL_OFF_LOW_SUPPLY_VOLT = 7 | *Off-Low Building Static Pressure
[12 empty] | COOL_OFF_LOW_AMBIENT = 8 | *Off-Economizer Damper Position
COOL_OFF_LOW_AMBIENT_PRE_RUN_DELAY = 9
[12 empty] | COOL_OFF_WAITING_CHANGEOVER 10 | *Disabled
[12 empty] | COOL_OFF_FREE_COOLING 11 | *Controlled by IAQ
[12 empty] | COOL_COMFORT_VENT 12 | *Diff. Between IAQ & OAQ
[12 empty] | *29615 | *Unreliable
[12 empty] | CLG_1_OFF_IDLE = 0 | *Return Air Temp
[12 empty] | CLG_1_ON_MIN_ON_TIME = 1 | *Local Input
[12 empty] | CLG_1_ON_NORMAL_CMD = 2 | *Network Sensor
[12 empty] | CLG_1_OFF_CLG_DISABLED = 3 | *BAS Override
[12 empty] | CLG_1_OFF_OAT_CUTOUT = 4 | *Not Available
CLG_1_OFF_LOW_AMBIENT_TEMP = 5
CLG_1_OFF_LOW_SUPPLY_VOLT = 6
CLG_1_OFF_HIGH_PRESSURE_LOCK = 7
CLG_1_OFF_LOW_PRESSURE_LOCK = 8
CLG_1_OFF_FREEZE_CONDITION = 9
CLG_1_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_1_OFF_COOLING_STAGE_DISABLED = 11
*29616
CLG_2_OFF_IDLE = 0
CLG_2_ON_MIN_ON_TIME = 1
CLG_2_ON_NORMAL_CMD = 2
CLG_2_OFF_CLG_DISABLED = 3
CLG_2_OFF_OAT_CUTOUT = 4
CLG_2_OFF_LOW_AMBIENT_TEMP = 5
CLG_2_OFF_LOW_SUPPLY_VOLT = 6
CLG_2_OFF_HIGH_PRESSURE_LOCK = 7
CLG_2_OFF_LOW_PRESSURE_LOCK = 8
CLG_2_OFF_FREEZE_CONDITION = 9
CLG_2_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_2_OFF_COOLING_STAGE_DISABLED = 11
*29617
CLG_3_OFF_IDLE = 0
CLG_3_ON_MIN_ON_TIME = 1
CLG_3_ON_NORMAL_CMD = 2
CLG_3_OFF_CLG_DISABLED = 3
CLG_3_OFF_OAT_CUTOUT = 4
CLG_3_OFF_LOW_AMBIENT_TEMP = 5
CLG_3_OFF_LOW_SUPPLY_VOLT = 6
CLG_3_OFF_HIGH_PRESSURE_LOCK = 7
CLG_3_OFF_LOW_PRESSURE_LOCK = 8
CLG_3_OFF_FREEZE_CONDITION 9
CLG_3_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_3_OFF_COOLING_STAGE_DISABLED = 11
*29618
CLG_4_OFF_IDLE = 0
CLG_4_ON_MIN_ON_TIME = 1
CLG_4_ON_NORMAL_CMD = 2
CLG_4_OFF_CLG_DISABLED = 3
CLG_4_OFF_OAT_CUTOUT = 4
CLG_4_OFF_LOW_AMBIENT_TEMP = 5
CLG_4_OFF_LOW_SUPPLY_VOLT = 6
CLG_4_OFF_HIGH_PRESSURE_LOCK = 7
CLG_4_OFF_LOW_PRESSURE_LOCK = 8
CLG_4_OFF_FREEZE_CONDITION = 9
CLG_4_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_4_OFF_COOLING_STAGE_DISABLED = 11
*29803
UNIT_IDLE = 0
UNIT_SD_ALARM = 1
UNIT_PURGE_COMMAND = 2
UNIT_SELF_TEST = 3
UNIT_MORNING_WARM_UP= 4
UNIT_AIR_TEMPERING = 5
UNIT_DEHUMIDIFICATION = 6
UNIT_HEATING = 7
UNIT_COOLING = 8
UNIT_ECONOMIZER = 9
UNIT_FAN_ONLY = 10
UNIT_COMFORT_VENTILATION = 11
*29708
HEAT_OFF_IDLE = 0
HEAT_ON_DEFROST = 1
HEAT_SAT_TEMPERING = 2
HEAT_MORNING_WARMUP = 3
HEAT_TSTAT_HEATING = 4
HEAT_UNOCC_HEATING = 5
HEAT_OCC_HEATING = 6
HEAT_OFF_DISABLED = 7
HEAT_OFF_OAT_LOCKOUT = 8
HEAT_OFF_SAT_LIMIT = 9
HEAT_OFF_WAITING_FOR_CHANGEOVER = 10
HEAT_COMFORT_VENTILATION = 11
*29750
ECONOMIZER_DISABLED = 0
ECONOMIZER_DAMPER_NOT_FUNCTIONAL = 1
ECONOMIZER_PURGE = 2
ECONOMIZER_UNAVAIL_SENSOR_FAULT = 3
ECONOMIZER_ECON_LOADING = 4
ECONOMIZER_SAT_HIGH_LIMIT = 5
ECONOMIZER_MIXED_AIR_LL = 6
ECONOMIZER_DEMAND_VENT_AIR_QUALITY = 7
ECONOMIZER_OUTDOOR_AIRFLOW_CNTL = 8
ECONOMIZER_FREE_CLG_IS_AVAIL = 9
ECONOMIZER_MIN_POSITION = 10
ECONOMIZER_TEST = 11
ECONOMIZER_COMFORT_VENTILATION = 12
ECONOMIZER_LOW_OA_AMBIENT = 13
*29777
EXHAUST_FAN_OFF_IDLE = 0
EXHAUST_FAN_ON_NORMAL_COMMAND = 1
EXHAUST_FAN_OFF_DISABLED = 2
EXHAUST_FAN_OFF_VFD_FAULT = 3
EXHAUST_FAN_OFF_LOW_BLDG_STATIC_PRESSURE = 4
EXHAUST_FAN_OFF_ECON_DAMPTER_POS = 5
*29791
HOT_GAS_OFF_IDLE = 0
HOT_GAS_ON_NORMAL_COMMAND = 1
HOT_GAS_ON_ALT_OPERATION_CMD = 2
HOT_GAS_OFF_DISABLED = 3
*29735
Htg_1_OFF_IDLE = 0
Htg_1_ON_DEFROST = 1
Htg_1_SAT_TEMPERING = 2
Htg_1_MORNING_WARMUP = 3
Htg_1_TSTAT_HEATING = 4
Htg_1_UNOCC_HEATING = 5
Htg_1_OCC_HEATING = 6
Htg_1_OFF_DISABLED = 7
Htg_1_OFF_OAT_LOCKOUT = 8
Htg_1_OFF_SAT_LIMIT = 9
Htg_1_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_1_COMFORT_VENTILATION = 11
*29736
Htg_2_OFF_IDLE = 0
Htg_2_ON_DEFROST = 1
Htg_2_SAT_TEMPERING = 2
Htg_2_MORNING_WARMUP = 3
Htg_2_TSTAT_HEATING = 4
Htg_2_UNOCC_HEATING = 5
Htg_2_OCC_HEATING = 6
Htg_2_OFF_DISABLED = 7
Htg_2_OFF_OAT_LOCKOUT = 8
Htg_2_OFF_SAT_LIMIT = 9
Htg_2_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_2_COMFORT_VENTILATION = 11
*29737
Htg_3_OFF_IDLE = 0
Htg_3_ON_DEFROST = 1
Htg_3_SAT_TEMPERING = 2
Htg_3_MORNING_WARMUP = 3
Htg_3_TSTAT_HEATING = 4
Htg_3_UNOCC_HEATING = 5
Htg_3_OCC_HEATING = 6
Htg_3_OFF_DISABLED = 7
Htg_3_OFF_OAT_LOCKOUT = 8
Htg_3_OFF_SAT_LIMIT = 9
Htg_3_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_3_COMFORT_VENTILATION = 11
*32578
ISO 10646
ASI X3.4
Micosoft DBCS Code
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool.
Note on B5: cedmonja: This point will occupy and unoccupy the unit through bacnet.
Note on B6: Chad Edmondson: UCB OCC 24 VAC input status; Occupied indicates 24 VAC input to the OCC terminal, Unoccupied indicates 0 VAC input to the OCC terminal.
Note on B7: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B8: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B9: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B11: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B15: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B16: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B17: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B18: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B19: Chad Edmondson: By default "YES" the PID tuning parameters are managed by PRAC+(Pattern Recognition Adaptive Control) algorithm base on either Zone Temperature or Discharge Air Temperature process. PRAC+ can be turned off by changing the value of Cooling Adaptive Tuning Enable to "NO". Doing this will setup the PID to use the process defaults for either Zone Temperature or Discharge Temperature which can be found in the Cooling Adaptive Tuning chart attached to the right.
Note on B23: Chad Edmondson: Point is defaulted to "YES". This will prevent unit operation during unoccupied mode. Set to "NO" if you want to operate unit during unocc mode.
Note on B25: Chad Edmondson: SSE board is default to ISO 10646. Using another encoding type could prevent seeing bacnet point descriptions. You will need to change to the Encoding type your device is using.
Note on B29: cedmonja: Variable speed- Sets the SSE board to operate as a VAV unit and control fan speed according to static pressure. Fixed Variable-Sets the SSE board to operate according to a 7 fan speed selection when the blower is VFD controlled. Single Speed-Sets the SSE Board to operate according to 100% fan operation. With no VFD applied to RTU.
Note on B30: cedmonja: None-Sets board not to recognize APS if not being used. Variable-allows operation of APS applied to a SSE VAV setup.
Note on B32: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B38: cedmonja: Commands fan to run continuous in a occupied mode when set to "YES".
Note on B45: Chad Edmondson: When RTU is a Heat pump the minimum stage setting is 2.
Note on B46: Chad Edmondson: Must equal number of cooling stages when applied to an RTU.
Note on B48: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B49: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B50: cedmonja: If Cooling OAT Cutout Enble is Yes, the compressor is not permitted if the OAT is less than the cooling OAT Cutout. If Cooling OAT Cutout Enable is NO. the compressor cycles 10 minutes On and 5 minutes Off if the OAT is less than the LowAmb10On5Off Setpoint. If a compressor is in the 10 min On cycle and the evaportator temperature (EC1 thru EC4) drops below 26 degrees F. the compressor output de-endergizes and the 5 minute ASCD starts. After 5 minutes ASCD expires, the compressor ouput is permitted. Anytime the compressor output de-energizes due to the evaporator coil temperature protection it does not count towards a hard compressor lockout.
Note on B54: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B80: cedmonja: Setpoint does not allow heating operation when Operational OAT goes above the setpoint.
Note on B89: Chad Edmondson: 2-10VDC output status.
Note on B90: Chad Edmondson: sets action of 4-stage board modulating Htg 2-10 VDC output; No sets modulating Htg output at 2 VDC is 0%/closed and at 10 VDC is 100%/open. Yes sets modulating Htg output at 10 VDC is 0%/closed and at 2 VDC is 100%/open.
Note on B95: Chad Edmondson: Freezestat Alarm A freezestat must be field-supplied and field-installed. When 24 VAC is not present on terminal FSHW and: • the outdoor air temperature is greater than 40°F, no action is taken and the unit operates normally • the outdoor air temperature is 40° F or less, the hot water valve opens 100%, the indoor fan de-energizes, the economizer outside air damper is fully closed, and all other fans de-energize. • The control returns to normal if either: • 24 VAC is present on terminal FSHW, or • the outdoor air temperature rises above 40°F
Note on B96: Chad Edmondson: Staged- Set for gas or electric staged heating. Proportional- Set for modulating heating output 2-10VDC for hydronic or steam heat.
Note on B99: cedmonja: Yes-enables economizer function. No-disables economizer function.
Note on B102: cedmonja: Value displays % economizer damper is open.
Note on B103: cedmonja: Economizer damper minimum % open setpoint during occupied mode.
Note on B104: cedmonja: Dry bulb economizer setpoint. When OAT drops below set point economizer functions starts.
Note on B105: cedmonja: Yes-Economizer free cooling is available. No-Economizer free cooling is not available.
Note on B106: cedmonja: Option A-(Do Not Use) Economizer damper position and/or time triggers compressor operation to supplement free cooling. Option B- Supply air temperature with VAV supply air temperature(upper/lower) setpoint triggers compressor operation to supplement free cooling.
Note on B107: cedmonja: Yes-Does not allow compressor operation during free cooling. No-allows compressor operation durig free cooling.
Note on B108: cedmonja: Single enthalpy free cooling setpoint. When Outside Air Enthalpy is below setpoint free cooling is available.
Note on B110: Chad Edmondson: Setpoint used to control SAT in economize setup set to Mechanical Option B CV Sensor. CV Option B Occupied With free cooling available and the operating space temperature is greater than the operating cooling setpoint, the dampers modulate to control the Upper SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes, then the dampers moduate to control to the Lower SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes and SAT is greater than the Lower SAT Setpoint +5°F, the first compressor output energizes. If the economizer position remains at 100% for another 5 minute time period, and the SAT is greater than the Lower SAT Setpoint +5°F, the second compressor output energizes. This process repeats every 5 minutes as long as the economizer position is at 100% until all the compressors energize. If the economizer position drops below 100% and does not reach minimum position, and returns to 100% and remains for 5-minutes, and the SAT is greater than the Lower SAT Setpoint +5°F, the next available compressor energizes and additional compressors energize until all the compressors energize. Any time the economizer remains at minimum position for 5 consecutive minutes, or SAT is lower than the Lower SAT Setpoint -5°F, the last energized compressor turns Off. If it remains at minimum position or SAT remains lower than the Lower SAT Setpoint -5°F, the compressors de-energize every 5 minutes until all are Off. If all compressor outputs de-engerize and the economizer modulates to control to Upper SAT Setpoint +/-0.5°F. When the cooling demand ends the compressors de-energize immediately and the dampers return to operating minimum position.
Note on B111: Chad Edmondson: Setpoint used to control SAT in economize setup set to Mechanical Option B CV Sensor. CV Option B Occupied With free cooling available and the operating space temperature is greater than the operating cooling setpoint, the dampers modulate to control the Upper SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes, then the dampers moduate to control to the Lower SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes and SAT is greater than the Lower SAT Setpoint +5°F, the first compressor output energizes. If the economizer position remains at 100% for another 5 minute time period, and the SAT is greater than the Lower SAT Setpoint +5°F, the second compressor output energizes. This process repeats every 5 minutes as long as the economizer position is at 100% until all the compressors energize. If the economizer position drops below 100% and does not reach minimum position, and returns to 100% and remains for 5-minutes, and the SAT is greater than the Lower SAT Setpoint +5°F, the next available compressor energizes and additional compressors energize until all the compressors energize. Any time the economizer remains at minimum position for 5 consecutive minutes, or SAT is lower than the Lower SAT Setpoint -5°F, the last energized compressor turns Off. If it remains at minimum position or SAT remains lower than the Lower SAT Setpoint -5°F, the compressors de-energize every 5 minutes until all are Off. If all compressor outputs de-engerize and the economizer modulates to control to Upper SAT Setpoint +/-0.5°F. When the cooling demand ends the compressors de-energize immediately and the dampers return to operating minimum position.
Note on B112: Chad Edmondson: Operation details include: Economizer loading function works only when only one compressor is operating. If SAT is less than the SAT Low Limit Setpoint and the operating OAT is greater than 60°F, the economizer output increases to control the SAT to the Operating SAT Setpoint +/-0.5°F.
Note on B113: Chad Edmondson: California Title 24 fault detection requirement. Setting this point to off will eliminate the feedback alarm "Econ Not Modulating".
Note on B116: cedmonja: With the series 10 & 20 RTU the only curren option is Non-Modulating Power Exhaust.
Note on B128: cedmonja: Demand Ventilation mode selection. Disabled-No Demand Ventilation Function. Controlled by IAQ- Enables Demand Ventilation control with IAQ input. Differential between IAQ & OAQ- Enables Demand Ventilation control with a comparison between IAQ & OAQ.
Note on B132: cedmonja: IAQ sensor range.
Note on B139: cedmonja: This point will reflect the offset + or - range of the occupied heating setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B140: cedmonja: This point will reflect the offset + or - range of the occupied cooling setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B141: cedmonja: Reading from Space Sensor connect to the ST, Com & SSO terminal.
Note on B145: cedmonja: The source of the space setpoint offset in use; Local is from UCB SSO 0-20,000 Ω input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates SSO input is currently not present.
Note on B164: cedmonja: the source of the indoor air quality input in use; Local is from the economizer board IAQ 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates IAQ input is currently not present
Note on B165: cedmonja: The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present.
Note on B166: cedmonja: the source of the outdoor air quality input in use; Local is from economizer board OAQ 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
Note on B169: cedmonja: Operation: The Air Monitor Station will be wired to the JCI Economizer Module and accepts a 0-10VDC input at the FR ARI terminals. Below shows the wiring terminals and economizer module. The Fresh Air Max Sensor Range must match the range of the Air Monitoring Station on the unit. When the Fresh Air Intake value falls below the fresh air intake setpoint the economizer damper position increase above the minimum position until the fresh air intake value equals the fresh air intake setpoint +/- 40 CFM. When the fresh air intake value rises above the fresh air intake setpoint the economizer damper position decreases until the fresh air intake value equals the fresh air intake setpoint or it reaches Minimum position setpoint. Note: The low ambient minimum position may force the damper position below the current setpoint and disables the air monitoring station reset.
Note on B175: cedmonja: Normal Occupied Operation Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 output energizes and the AUX-HGR output energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 output energizes but the AUX-HGR output de-energizes. Any additional cooling demands energize compressor outputs, but do not change the status of the AUX-HGR output. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas
Note on B176: cedmonja: Alternate Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for both first and second cooling stages and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and C2 outputs energize and AUX-HGR de-energizes. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas Reheat Humidity Setpoint.
Note on B178: cedmonja: YES- Allows access to hot gas reheat mode selection in HGRAlt-En. NO-Does not allow access to hot gas reheat mode selection in HGRAlt-En.
Note on B179: cedmonja: YES- Allows hot gas reheat operation when occupancy status is Unoccupied. NO- Does not allow hot has reheat operation when occupancy status is Unoccupied.
Note on B184: cedmonja: The number of heat pump stages; 1 or more enabled the UCB H1 VAC output to position reversing valve, 2 ormore enabled the UCB H2 VAC output to initiate supplemental heat.
Note on B188: cedmonja: Cooling: Cooling calls are handled the same way as non-heat pump cooling units with one exception. Exception: During cooling, the control energizes the H1 output to turn on the Reversing Valve. The H1 output to the reversing valve remains energized between calls for cooling. If a heating call arises, the H1 output turns off. Heating: If a first stage of heating is called for (thermostat or zone sensor/network), all available compressors stage on, with a 30 second time delay between compressors. The Cooling Fan On Delay and Cooling Fan Off Delay are used for the first stage of heat pump heating. During a first stage of heating, the H1 output turns off and remain off between heat calls. If a second stage of heating is called for, the H2 or AUX output energizes the Emergency/Aux heating. If a thermostat calls for W2 only, only the H2 output energizes. The Heating Fan On Delay and Heating Fan Off Delay are used.

## RTU-FixedVariable
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point/ *Enum drop down list | Type | Modbus Point | Read/Write | Settting value/ *drop down list
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level |  | Set at board level |  | 4 to 127
|  | OccMode | Commission>HVACZone>OccMode | 29518 | MV | 82 | Read/Write | External/ Schedule
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | MV | 84 | Read/Write | Occupied/ Unoccupied
|  | Occupancy Binary Input | Details>Service>Inputs>BinaryInputs>Occ | 29516 | MV | 291 | Read | Occupied/ Unoccupied
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | MV | Set at board level |  | "Yes" or "No"
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level |  | Set at board level |  | *Modbus Field Bus
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | MV | Set at board level |  | OFF / ON
|  | Alarms | Alarms |  |  |  |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level |  | Set at board level |  | defaulted to 1
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level |  | Set at board level |  | Auto or 1200-76800
|  | Unit Name | Details>Unit>Name | Set at board level |  | Set at board level |  |  | Cooling Adaptive Tuning Default Parameters- Not Adjustable
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level |  | View at Board level |  | Current Version 3.0.0.1072 | Default Tuning Parameters
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level |  | Set at board level |  | "TRUE" or "FALSE" |  | Initial Prop Band | Intergral Time (sec)
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | MV | 292 | Read | Occupied/ Unoccupied | Zone- T | 4.2 | 892
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | AV | 80 | Read/Write | ON/OFF | DA-T | 21.8 | 203
|  | Self Test | Self Test>Start | Set at board Level |  | Set at board level |  | *Start
|  | Cooling Adaptive Tuning Enabled | Details>Control>Clg>Setup>ClgAdapTunEn | 29882 | MV | 100 | Read/Write | "Yes" or "No"
|  | Heating Adaptive Tuning Enabled | Details>Control>Htg>Setup>HtgAdapTunEn | 29881 | MV | 114 | Read/Write | "Yes" or "No"
|  | Time | Update>Time | Set at Board Level |  | Set at board level |  | 24 hours Military Format
|  | Unit Status | Status>Unit-S | *29803 | MV | 280 | Read
|  | Off During Unoccuped Mode | Commision>HVACzone>OffDurUnocc | 29914 | MV | 88 | Read/Write | "Yes" or "No"
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>RTU | Set at board level |  |  |  | *RTU
|  | Bacnet Encoding Type | Controller>Network>EncodingType | *32578 | MV |  |  | 3.0.0.1116 Rev or higher
|  | Temporary Occupancy Timeout | Details>Zone>Indoor>TempOccTimeout | 29521 | AV | 85 | Read/Write | 30 to 120 min. time period
FAN SETUP/STATUS
|  | Fan Control | Summary>Fan>FanCtl-Type | 29555 | MV | Set at board level |  | Fixed Variable(8 speed fan selection)
|  | APS Setup | Details>Service>Factory>Standard>APS Setup | 29556 | MV | Set at board level |  | None or Constant
|  | APS Status | Details>Control>IndoorFan>Status>APS | 29557 | MV | 305 | Read | ON = APS closed
|  | Net Override Fan Request | Details>Service>Inputs>NetworkInputs>NetFanReq | 29536 | MV | 87 | Read/Write | OFF / ON
|  | Fan Only Command VFD speed % | Commission> IndoorFan>FanOnly-%Cmd | 29570 | AV | 12 | Read/Write | set to 0% to 100% speed reference
|  | 1 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>1ClgStg-%Cmd | 29571 | AV | 13 | Read/Write | set to 0% to 100% speed reference
|  | 1 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>1HtgStg-%Cmd | 29573 | AV | 17 | Read/Write | set to 0% to 100% speed reference
|  | 2 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>2ClgStg-%Cmd | 29572 | AV | 14 | Read/Write | set to 0% to 100% speed reference
|  | 2 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>2HtgStg-%Cmd | 29574 | AV | 18 | Read/Write | set to 0% to 100% speed reference
|  | 3 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>3ClgStg-%Cmd | 29819 | AV | 15 | Read/Write | set to 0% to 100% speed reference
|  | 3 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>3HtgStg-%Cmd | 29821 | AV | 19 | Read/Write | set to 0% to 100% speed reference
|  | 4 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>4ClgStg-%Cmd | 29820 | AV | 16 | Read/Write | set to 0% to 100% speed reference
|  | Fan "OFF" Delay Cool | Details>Control>IndoorFan>Setup.FanOffDlyCool | 29559 | AV | Set at board level |  | 0 to 255 second timer
|  | Fan "OFF" Delay Heat | Details>Control>IndoorFan>Setup>FanOffDlyHeat | 29561 | AV | Set at board level |  | 0 to 255 second timer
|  | Fan "OFF" Start Heat | Details>Control>IndoorFan>Setup>FanoffStartHeat | 29569 | MV | 92 | Read/Write | "YES" or "NO"
|  | Fan "ON" Delay Cool | Details>Control>IndoorFan>Setup>FanOnDlyCool | 29558 | AV | 90 | Read/Write | 0 to 30 second timer
|  | Fan "ON" Delay Heat | Details>Control>IndoorFan>Setup>FanOnDlyHeat | 29560 | AV | Set at board level |  | 0 to 30 second timer
|  | Fan "ON" Occupied | Details>Control>IndoorFan>Setup>FanOnOcc | 29568 | MV | 91 | Read/Write | "YES" or "NO"
|  | Fan Overload | Details>Control>IndoorFan>Setup>FanOvrload | 29553 | MV | 304 | Read
|  | Fan Status | Status>Fan-S | *29550 | MV | 302 | Read
|  | Fan VFD Status | Summary> Fan> FanVFD | 29551 | AV | 157 | Read
|  | Fan VFD Fault | Details>Control>IndoorFan>Status>FanVFDFlt | 29552 | MV | 303 | Read
COOLING SETUP/STATUS
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | MV | 93 | Read/Write | "YES" or "NO"
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | AV | 263 | Read | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | AV | Set at board level |  | 1 to 4
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | AV | 32 | Read/Write | 1 to 4 Circuits
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | MV | Set at board level |  | "YES" or "NO"
|  | Hot Gas Bypass Installed (Present) | Details>Service>Factory>Standard>HGP-Inst | 29623 | MV | Set at board level |  | "YES" or "NO"
|  | Cooling Status | Status>Clg-S | *29577 | MV | 308 | Read | Displays Cooling Status
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | MV | 94 | Read/Write | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | AV | 21 | Read/Write | 0 to 100 degrees
|  | Low Ambient Enabled | Details>Control>Clg>Setup>LowAmb-En | 29928 | MV | Set at board level |  | "YES" or "NO"
|  | Low Ambient Operation Setpoint | Detials>Control>Clg>Setup>LowAmb10On5OffSp | 29585 | AV | Set at board level |  | 0 to 60 degrees
|  | Constant Volume Occupied Cooling Setpoint | Details>Setpoints>ClgOcc-Sp | 29608 | AV | 29 | Read/Write | range 45 to 98 degrees
|  | Constant Volume Unoccupied Cooling Setpoint | Details>Setpoints>ClgUnocc-Sp | 29609 | AV | 30 | Read/Write | range 46 to 99 degress
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | MV | 98 | Read/Write | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | AV | 25 | Read/Write | 40 to 65 degrees
|  | Compressor 1 Command | Details>Control>Clg>Stage 1>C1-Cl | 29611 | MV | 311 | Read
|  | Compressor 1 Status | Details>Control>Clg>Stage1>C1-S | *29615 | MV | 312 | Read
|  | Compressor 1 Enabled | Details>Control>Clg>Stage1>C1-En | 29619 | MV | 101 | Read
|  | Compressor 1 Accumulated Run Time | Details>Control>Clg>Stage1>C1RunTim | 29627 | AV | 33 | Read/Write
|  | Compressor 2 Command | Details>Control>Clg>Stage2>C2-Cl | 29612 | MV | 319 | Read
|  | Compressor 2 Status | Details>Control>Clg>Stage2>C2-S | *29616 | MV | 320 | Read
|  | Compressor 2 enabled | Details>Control>Clg>Stage2>C2-En | 29620 | MV | 120 | Read
|  | Compressor 2 Accumulated Run time | Details>Control>Clg>Stage2>C2RunTim | 29628 | AV | 34 | Read/Write
|  | Compressor 3 Command | Details>Control>Clg>Stage3>C3-Cl | 29613 | MV | 327 | Read
|  | Compressor 3 Status | Details>Control>Clg>Stage3>C3-S | *29617 | MV | 328 | Read
|  | Compressor 3 Enabled | Details>Control>Clg>Stage3>C3-En | 29621 | MV | 103 | Read/Write
|  | Compressor 3 Accumulated Run Time | Details>Control>Clg>Stage3>C3RunTim | 29629 | AV | 35 | Read/Write
|  | Compressor 4 Command | Details>Control>Clg>Stage4>C4-Cl | 29614 | MV | 335 | Read
|  | Compressor 4 Status | Details>Control>Clg>Stage4>C4-S | *29618 | MV | 336 | Read
|  | Compressor 4 Enabled | Details>Control>Clg>Stage4>C4-En | 29622 | MV | 104 | Read
|  | Compressor 4 Accumulated Run Time | Details>Control>Clg>Stage4>C4RunTim | 29630 | AV | 36 | Read/Write
HEATING SETUP/STATUS
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | MV | 105 | Read/Write | "YES" or "NO"
|  | Heating Status | Status>Htg-S | *29708 | MV | 347 | Read
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | AV | 264 | Read | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | AV | Set at board level |  | 1 to 3
|  | Heating OAT Cutout Setpoint | Details>Control>Htg>Setup>HtgOATCutout-Sp | 29711 | AV | 38 | Read/Write | 0 to 100 degrees
|  | Constant Volume Occupied Heating Setpoint | Details>Setpoints>CVHtgOcc-Sp | 29728 | AV | 42 | Read/Write | Range 46 to 99 degrees
|  | Constant Volume Unoccuped Heating Setpoint | Details>Setpoints>CVHtgUnocc-Sp | 29729 | AV | 43 | Read/Write | Range 45 to 98 degrees
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29739 | AV | 49 | Read/Write
|  | Heating Stage 1 Command | Details>Control>Htg>Stage1>H1 | 29732 | MV | 352 | Read
|  | Heating Stage 1 Status | Details>Cotrol>Htg>Stage1>H1-S | *29735 | MV | 360 | Read
|  | Heating Stage 2 Command | Details>Control>Htg>Stage2>H2 | 29733 | MV | 361 | Read
|  | Heating Stage 2 Status | Details>Cotrol>Htg>Stage2>H2-S | *29736 | MV | 362 | Read
|  | Heating Stage 3 Command | Details>Control>Htg>Stage3>H3 | 29734 | MV | 363 | Read
|  | Heating Stage 3 Status | Details>Cotrol>Htg>Stage3>H3-S | *29737 | MV | 364 | Read
|  | Supply Air Heating Limit Enabled | Detals>Control>Htg>Setup>SATHtgLimit-En | 29709 | MV | 106 | Read/Write | "YES" or "NO"
|  | Supply Air Heating Limit Set point | Details>Control>Htg>Setup>SATHtgLimt-Sp | 29710 | AV | 37 | Read/Write | 100 degree to 180 degree
|  | Hot Water Heat Valve % Output (4 stage Exp Board) | Details>Control>Htg>Status>HWV | 29741 | AV | 252 | Read | 0 to 100%
|  | Hot Water Valve Rev Acting (4 stage Exp. Board) | Details>Control>Htg>Setup>HydReverse | 29742 | MV | 115 | Read/Write | "YES" or "NO"
|  | Hot Water Htg Stage 1 SAT Sp (4 stage Exp. Board) | Details>Control>Htg>Setup>HydH1SA-Sp | 29743 | AV | 51 | Read/Write | 80 to 180 degrees
|  | Hot Water Htg Stage 2 SAT Sp ( 4 stage Exp. Board) | Details>Control>Htg>Setup>HydH2SA-Sp | 29744 | AV | 52 | Read/Write | 80 to 180 degrees
|  | Hot Water Heat SAT Tempering Enabled (4 stage Exp. Board) | Details>Control>Htg>SATTempHydHt-En | 29745 | MV | 116 | Read/Write | "Yes" or "No"
|  | Hot Water Heat SAT Tempering Set Point (4 stage Exp. Board) | Commission>Htg>SATTempHydHt-Sp | 29746 | AV | 53 | Read/Write
|  | Hot Water Freeze Stat (4 stage Exp. Board) | Details>Service>Inputs>BinaryInputs>Limit>FSHW | 29712 | MV | 348 | Read | Normal or Alarm
|  | Heating Control Type | Details>Control>Htg>Status>Htg-Type | Set at board Level |  | Set at board level |  | Staged or Proportional
ECONOMIZER SETUP/STATUS
|  | Economizer Enabled | Commission>Econ>Econ-En | 29747 | MV | 118 | Read/Write | "YES" or "NO"
|  | Economizer Status | Status>Econ-S | *29750 | MV | 370 | Read
|  | Economizer Firware | Controller>SysCntrls>Econ>EconMainVer | N/A |  | N/A |  | View at board level or Map Gateway
|  | Economizer Damper Position | Details>Service>Inputs>Sensors>EconDampPos | 29748 | AV | 253 | Read | % open
|  | Economizer Minimum Position | Details>Control>Econ>Setup>Econ-MinPos | 29759 | AV | 77 | Read/Write | % Open Set point
|  | Economizer OAT Set point | Details>Control>Econ>Setup>EconOAT-SpEn | 29753 | AV | 55 | Read/Write | 40 to 80 degrees
|  | Economizer Free Cooling Available | Summary>Econ>Econ-Free | 29749 | MV | 369 | Read | "YES" or "NO"
|  | Economizer Mechanical Setup | Details>Control>Econ>Setup>EconMechStp | 29912 | MV | Set at board level |  | Option B
|  | All Compressor OFF-Economizer | Details>Control>Clg>Setup>AllCompOff-Econ | 29584 | MV | 96 | Read/Write | "YES" or "NO"
|  | Econ OA Enthalpy Setpoint | Details>Control>Econ>Setup>EconOAEth-Sp | 29754 | AV | 56 | Read/Write | 10 to 50 BTU/Lb
|  | Free Cooling Selection | Details>Control>Econ>Setup>FreeClg-Sel | 29752 | MV | 119 | Read/Write | * Auto
|  | Low Ambient Minimum Position | Details>Control>Econ>Setup>LowAmb-MinPos | 29756 | AV | 58 | Read/Write | 0% to 100% econ damper open
|  | Low Ambient Set point | Details>Control>Econ>Setup>LowAmb-Sp | 29755 | AV | 57 | Read/Write | 0 to 60 degrees
|  | Low Speed Fan Minimum Position | Details>Control>Econ>Setup>LowSpeedFan-MinPos | 29808 | AV | 54 | Read/Write | 0% to 100% econ damper open
|  | VAV Clg SA Upper Stpt | Details>Setpoints>SATUp-Sp | 29604 | AV | 26 | Read/Write | 60 degree
|  | VAV Clg SA Lower Stpt | Details>Setpoints>SATLo-Sp | 29605 | AV | 27 | Read/Write | 55 degree
|  | Economizer Loading Enabled | Details>Control>Clg>Setup>EconLoad-En | 29583 | MV | 95 | Read/Write | "YES" or "NO"
|  | Economzer Fault Detection Enable | Commission>Econ>EconFltDetectEn | 29915 | MV | 132 | Read/Write | Disable/Enable
Power Exhaust Setup/STATUS
|  | Power Exhaust Fan Type | Details>Service>Factory>Econ>ExFType | 29774 |  | set at board level |  | *None
|  | Power Exhaust Fan Command | Details>Control>PowerEx>Status> | 29775 | MV | 376 | Read
|  | Power Exhaust Fan Status | Details>Control>PowerEx>Status>ExFan | *29777 | MV | 377 | Read
|  | Power Exhaust Modulating Damper Output | Summary>PowerEx>EAD-O | 29782 | AV | 261 | Read
|  | Building Pressure Set Point | Summary>PowerEx>Bldg-Sp | 29780 | AV | 63 | Read/Write
|  | Econ Damper Position Power Exhaust "OFF" | Summary>PowerEx>EconDmpPosFanOff | 29786 | AV | 67 | Read/Write
|  | Econ Damper Position Power Exhaust "ON" | Summary>PowerEx>EconDmpPosFanOn | 29785 | AV | 66 | Read/Write
|  | Power Exhaust Damper Position "OFF" | Commission>PoweEx>ExDmpPosFanOff | 29784 | AV | 65 | Read/Write
|  | Power Exhaust Damper Position "On" | Commission>PoweEx>ExDmpPosFanOn | 29783 | AV | 64 | Read/Write
|  | Power Exhaust VFD Output Status | Summary>PowerEx>ExFanVFD | 29776 | AV | 258 | Read
CO2 Demand Ventilation Setup/STATUS
|  | (CO2) Demand Ventilation Mode | Commission>Dvent>Dvent-Mode | 29765 | MV | 120 | Read/Write | *Disabled
|  | (CO2) Demand Ventilation Mode IAQ Set Point | Commission>Dvent>DventIAQ-Sp | 29767 | AV | 61 | Read/Write | 0 to 5000 ppm
|  | (CO2) Demand Ventilation Max Econ Damper Position | Commission>Dvent>DVentMaxEconPos | 29766 | AV | 60 | Read/Write | range 0% to 100% open
|  | (CO2) OAQ Range | Commission>Dvent>OAQRange | 29548 | MV | 301 | Read | 0 ppm to 5000 ppm
|  | (CO2) IAQ Range | Commission>Dvent>IAQRange | 29529 | AV | 294 | Read | 0 ppm to 5000 ppm
|  | (CO2) Demand Ventilation Differential Set Point | Commission>Dvent>DVentDiff-Sp | 29768 | AV | 62 | Read/Write | 0 ppm to 5000 ppm
Sensor Inputs & Readings
|  | Supply Air Temperature | Details>Service>Inputs>Sensors>SAT | 29564 | AV | 158 | Read
|  | Return Air Temperature | Details>Service>Inputs>Sensors>RAT | 29764 | AV | 139 | Read
|  | Operational Outdoor Air Temperature | Details>Zone>Outdoor>OprOAT | 29541 | AV | 153 | Read
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29730 | AV | 251 | Read
|  | Constant Volume Operating Cooling Setpoint | Details>Setpoints>OprCVClg-Sp | 29610 | AV | 287 | Read
|  | Operational Space Temperature | Details>Zone>Indoor>OprST | 29522 | AV | 135 | Read
|  | Operational Space Sensor Offset | Details>Zone>Indoor>OprSSO | 29537 | AV | 140 | Read
|  | Space Temperature Source | Details>Zone>Indoor>STsrc | 29523 | MV | 293 | Read | *Return Air Temp
|  | Space Sensor Offset Range | Details>Zone>Indoor>SSORange | N/A |  | N/A |  | 0 to 5 degrees F setpoint
|  | Space sensor Offset Source | Details>zone>Indoor>SSOSrc | 29538 | MV | 294 | Read
|  | Space Humidity RAH input | Details>Control>Econ>Status>RAH | 29828 | AV | 138 | Read
|  | Outdoor Air Humidity Input | Details>Service>Inputs>Sensor>OAH | N/A |  | N/A
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OA-Enth | 29545 | AV | 155 | Read
|  | Return Air Enthalpy | Details>Control>Econ>Status>RA-Enth | 29763 | AV | 257 | Read
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531 | AV | 137 | Read
|  | Operational Outdoor Air Humidity | Details>Control>Econ>Status>OprOAH | 29544 | AV | 154 | Read
|  | Net Override Space Temperature | Details>Service>Inputs>NetworkInputs>NetST | 29526 | AV | 1 | Read/Write | Writable Point to Space Temp
|  | Net Override Outdoor Air Temperature | Details>Service>Inputs>NetworkInputs>NetOAT | 29543 | AV | 6 | Read/Write | Writable Point to OAT
|  | Net Override Indoor Air Quality | Details>Service>Inputs>NetworkInputs>NetIAQ | 29530 | AV | 3 | Read/Write | Writable Point to IAQ
|  | Net Override Outdoor Air Quality | Details>Service>Inputs>NetworkInputs>NetOAQ | 29549 | AV | 8 | Read/Write | Writable Point to OAQ
|  | Net Override Outdoor Air Humidity | Details>Service>Inputs>NetworkInputs>NetOAH | 29546 | AV | 7 | Read/Write | Writable Point to OAH
|  | Net Override Space Humidity | Details>Service>Inputs>NetworkInputs>NetSH | 29533 | AV | 4 | Read/Write | Writable Point to Space Humidity
|  | Net Override Space Sensor Offset | Details>Service>Inputs>NetworkInputs>NetSSO | 29540 | AV | 5 | Read/Write | Writable Point to Space Sensor offset
|  | Building Pressure | Summary>PowerEx>BldgPres | 29781 | AV | 260 | Read | (-).25 to .25"wc
|  | (CO2) IAQ Input | Details>Service>Inputs>Sensor>IAQ | N/A |  | N/A
|  | (CO2) OAQ Input | Details>Service>Inputs>Sensor>OAQ | N/A |  | N/A
|  | Operational IAQ | Summary>Dvent>OprIAQ | 29527 | AV | 136 | Read
|  | IAQ source | Details>Zone>Indoor>IAQsrc | 29528 | MV | 294 | Read
|  | Operational OAQ | Summary>Dvent>OprOAQ | 29547 | AV | 156 | Read
|  | OAQ source | Deatails>Zone>Outdoor>OAQsrc | 29548 | MV | 301 | Read
AIR MONITOR
|  | Fresh Air Enable | Details>Control>AirMonStation>FRSHAIR-EN | Set at board Level |  | Set at board level |  | Enable/Disable
|  | Fresh Air Flow Reading | Details>Control>AirMonStation>FR-Air | 29796 | AV | 262 | Read | CFM reading
|  | Air Monitor Flow Range | Details>Control>AirMonStation>MOA-Range | 29797 | AV | 70 | Read/Write | Range 0 to 50000 CFM
|  | Air Monitor Flow Setpoint | Details>Control>AirMonStation>MOAflow-Sp | 29795 | AV | 69 | Read/Write | Range 0 to 50000 CFM
HOT GAS REHEAT
|  | Hot Gas Reheat Enabled for Operation | Details>Service>Factory>Standard>HGR-En | 29789 | MV | 123 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Alternate Operation Enabled | Details>Control>HGR>HGRAlt-En | 29793 | MV | 124 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Gas Reheat Humidity Setpoint | Details>Control>HGR>HGRHum-SP | 29792 | AV | 68 | Read/Write | 0% to 100%
|  | Hot Gas Reheat Alternate Operation Writable | Details>Control>HGR>HGRAltWrite | 29794 |  | N/A | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Enabled for Unoccupied Operation | Details>Control>HGR>HGRUnocc-En | 29904 | MV | 133 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Unoccupied Humidity Setpoint | Details>Control>HGR>HGRUnoccHum-Sp | 29903 | AV | 78 | Read/Write | 0% to 100%
|  | Hot Gas Reheat Status | Details>Control>HGR>HGR-S | *29791 | MV | 380 | Read
HEAT PUMP |  | (Note: # of Heating and Cooling Stages will have to be adjusted appropriately for Heat Pump Operation)
|  | Heat Pump number of Stages | Details>Service>Factory>Standard>#HtPumpStgs | 29898 | AV | Set at board level |  | 1 to 2 stages
|  | Defrost Curve Set | Commission>Defrost>DefrostCurveSel | 29899 (Defrost State) | MV | 177 | Read/Write | Curve Selection 1 through 6
|  | Reversing Valve | Summary>HeatPump>RevVlv | 29900 |  | 366 | Read | Output Status
|  | Auxillary Heat | Summary>HeatPump>AuxHtg | 29901 |  | 367 | Read | Output Status
|  | Heat Pump Mode | Summary>HeatPump>Mode | 29902 |  | 368 | Read | Operating Status
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | AV | 32 | Read/Write
[12 empty] | *29550 | *Wired Field Bus = BACnet MSTP
[12 empty] | FAN_OFF_IDLE = 0 | *N2 Slave Field Bus
[12 empty] | FAN_ON_PURGE = 1 | *Modbus Field Bus
FAN_ON_GAS_VALVE = 2
[12 empty] | FAN_ON_DEFROST = 3 | *Start
[12 empty] | FAN_ON_THERMOSTAT_REQST = 4 | *Pause
[12 empty] | FAN_ON_FAN_OFF_DELAY_COOL = 5 | *Cancel
[12 empty] | FAN_ON_FAN_OFF_DELAY_HEAT = 6 | *Status
[12 empty] | FAN_ON_CONTINUOUS_FAN_OCC_OP = 7 | *Reset
FAN_ON_NORMAL_COMMAND = 8
[12 empty] | FAN_OFF_EXCEEDING_DUCT_PRESSURE = 9 | *Split
[12 empty] | FAN_OFF_LOW_VOLTAGE = 10 | *RTU
[12 empty] | FAN_OFF_FAN_OVERLOAD_LOCKOUT = 11 | *Heat Pump
[12 empty] | FAN_OFF_FAN_VFD_FAULT = 12 | *Unknown
FAN_OFF_HOT_WATER_FREEZE_STAT = 13
[12 empty] | FAN_OFF_AIR_PROVING_SWITCH = 14 | * Auto
[12 empty] | FAN_OFF_MIN_OFF_DELAY = 15 | * Dry Bulb
[12 empty] | FAN_OFF_FAN_ON_DELAY_HEAT = 16 | * Single Enthalpy
[12 empty] | FAN_OFF_FAN_ON_DELAY_COOL = 17 | * Dual Enthalpy
*None
[12 empty] | *29577 | *Non-Modulating
[12 empty] | COOL_OFF_IDLE = 0 | *Modulating Damper
[12 empty] | COOL_THERM_COOLING = 1 | *Variable Frequency Fan
COOL_UNOCC_COOLING = 2
[12 empty] | COOL_OCC_COOLING = 3 | *Off-Idle
[12 empty] | COOL_OFF_OAT_LOCKOUT = 4 | *On-Normal Command
[12 empty] | COOL_OFF_DISABLED = 5 | *Off-Disabled
[12 empty] | COOL_OFF_LOCKOUT= 6 | *Off-VFD Fault
[12 empty] | COOL_OFF_LOW_SUPPLY_VOLT = 7 | *Off-Low Building Static Pressure
[12 empty] | COOL_OFF_LOW_AMBIENT = 8 | *Off-Economizer Damper Position
COOL_OFF_LOW_AMBIENT_PRE_RUN_DELAY = 9
[12 empty] | COOL_OFF_WAITING_CHANGEOVER 10 | *Disabled
[12 empty] | COOL_OFF_FREE_COOLING 11 | *Controlled by IAQ
[12 empty] | COOL_COMFORT_VENT 12 | *Diff. Between IAQ & OAQ
[12 empty] | *29615 | *Unreliable
[12 empty] | CLG_1_OFF_IDLE = 0 | *Return Air Temp
[12 empty] | CLG_1_ON_MIN_ON_TIME = 1 | *Local Input
[12 empty] | CLG_1_ON_NORMAL_CMD = 2 | *Network Sensor
[12 empty] | CLG_1_OFF_CLG_DISABLED = 3 | *BAS Override
[12 empty] | CLG_1_OFF_OAT_CUTOUT = 4 | *Not Available
CLG_1_OFF_LOW_AMBIENT_TEMP = 5
CLG_1_OFF_LOW_SUPPLY_VOLT = 6
CLG_1_OFF_HIGH_PRESSURE_LOCK = 7
CLG_1_OFF_LOW_PRESSURE_LOCK = 8
CLG_1_OFF_FREEZE_CONDITION = 9
CLG_1_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_1_OFF_COOLING_STAGE_DISABLED = 11
*29616
CLG_2_OFF_IDLE = 0
CLG_2_ON_MIN_ON_TIME = 1
CLG_2_ON_NORMAL_CMD = 2
CLG_2_OFF_CLG_DISABLED = 3
CLG_2_OFF_OAT_CUTOUT = 4
CLG_2_OFF_LOW_AMBIENT_TEMP = 5
CLG_2_OFF_LOW_SUPPLY_VOLT = 6
CLG_2_OFF_HIGH_PRESSURE_LOCK = 7
CLG_2_OFF_LOW_PRESSURE_LOCK = 8
CLG_2_OFF_FREEZE_CONDITION = 9
CLG_2_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_2_OFF_COOLING_STAGE_DISABLED = 11
*29617
CLG_3_OFF_IDLE = 0
CLG_3_ON_MIN_ON_TIME = 1
CLG_3_ON_NORMAL_CMD = 2
CLG_3_OFF_CLG_DISABLED = 3
CLG_3_OFF_OAT_CUTOUT = 4
CLG_3_OFF_LOW_AMBIENT_TEMP = 5
CLG_3_OFF_LOW_SUPPLY_VOLT = 6
CLG_3_OFF_HIGH_PRESSURE_LOCK = 7
CLG_3_OFF_LOW_PRESSURE_LOCK = 8
CLG_3_OFF_FREEZE_CONDITION = 9
CLG_3_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_3_OFF_COOLING_STAGE_DISABLED = 11
*29618
CLG_4_OFF_IDLE = 0
CLG_4_ON_MIN_ON_TIME = 1
CLG_4_ON_NORMAL_CMD = 2
CLG_4_OFF_CLG_DISABLED = 3
CLG_4_OFF_OAT_CUTOUT = 4
CLG_4_OFF_LOW_AMBIENT_TEMP = 5
CLG_4_OFF_LOW_SUPPLY_VOLT = 6
CLG_4_OFF_HIGH_PRESSURE_LOCK = 7
CLG_4_OFF_LOW_PRESSURE_LOCK = 8
CLG_4_OFF_FREEZE_CONDITION = 9
CLG_4_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_4_OFF_COOLING_STAGE_DISABLED = 11
*29803
UNIT_IDLE = 0
UNIT_ALARM = 1
UNIT_PURGE_COMMAND = 2
UNIT_SELF_TEST = 3
UNIT_MORNING_WARM_UP= 4
UNIT_AIR_TEMPERING = 5
UNIT_DEHUMIDIFICATION = 6
UNIT_HEATING = 7
UNIT_COOLING = 8
UNIT_ECONOMIZER = 9
UNIT_FAN_ONLY = 10
UNIT_COMFORT_VENTILATION = 11
*29708
HEAT_OFF_IDLE = 0
HEAT_ON_DEFROST = 1
HEAT_SAT_TEMPERING = 2
HEAT_MORNING_WARMUP = 3
HEAT_TSTAT_HEATING = 4
HEAT_UNOCC_HEATING = 5
HEAT_OCC_HEATING = 6
HEAT_OFF_DISABLED = 7
HEAT_OFF_OAT_LOCKOUT = 8
HEAT_OFF_SAT_LIMIT = 9
HEAT_OFF_WAITING_FOR_CHANGEOVER = 10
HEAT_COMFORT_VENTILATION = 11
*29750
ECONOMIZER_DISABLED = 0
ECONOMIZER_DAMPER_NOT_FUNCTIONAL = 1
ECONOMIZER_PURGE = 2
ECONOMIZER_UNAVAIL_SENSOR_FAULT = 3
ECONOMIZER_ECON_LOADING = 4
ECONOMIZER_SAT_HIGH_LIMIT = 5
ECONOMIZER_MIXED_AIR_LL = 6
ECONOMIZER_DEMAND_VENT_AIR_QUALITY = 7
ECONOMIZER_OUTDOOR_AIRFLOW_CNTL = 8
ECONOMIZER_FREE_CLG_IS_AVAIL = 9
ECONOMIZER_MIN_POSITION = 10
ECONOMIZER_TEST = 11
ECONOMIZER_COMFORT_VENTILATION = 12
ECONOMIZER_LOW_OA_AMBIENT = 13
*29777
EXHAUST_FAN_OFF_IDLE = 0
EXHAUST_FAN_ON_NORMAL_COMMAND = 1
EXHAUST_FAN_OFF_DISABLED = 2
EXHAUST_FAN_OFF_VFD_FAULT = 3
EXHAUST_FAN_OFF_LOW_BLDG_STATIC_PRESSURE = 4
EXHAUST_FAN_OFF_ECON_DAMPTER_POS = 5
*29791
HOT_GAS_OFF_IDLE = 0
HOT_GAS_ON_NORMAL_COMMAND = 1
HOT_GAS_ON_ALT_OPERATION_CMD = 2
HOT_GAS_OFF_DISABLED = 3
*29735
Htg_1_OFF_IDLE = 0
Htg_1_ON_DEFROST = 1
Htg_1_SAT_TEMPERING = 2
Htg_1_MORNING_WARMUP = 3
Htg_1_TSTAT_HEATING = 4
Htg_1_UNOCC_HEATING = 5
Htg_1_OCC_HEATING = 6
Htg_1_OFF_DISABLED = 7
Htg_1_OFF_OAT_LOCKOUT = 8
Htg_1_OFF_SAT_LIMIT = 9
Htg_1_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_1_COMFORT_VENTILATION = 11
*29736
Htg_2_OFF_IDLE = 0
Htg_2_ON_DEFROST = 1
Htg_2_SAT_TEMPERING = 2
Htg_2_MORNING_WARMUP = 3
Htg_2_TSTAT_HEATING = 4
Htg_2_UNOCC_HEATING = 5
Htg_2_OCC_HEATING = 6
Htg_2_OFF_DISABLED = 7
Htg_2_OFF_OAT_LOCKOUT = 8
Htg_2_OFF_SAT_LIMIT = 9
Htg_2_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_2_COMFORT_VENTILATION = 11
*29737
Htg_3_OFF_IDLE = 0
Htg_3_ON_DEFROST = 1
Htg_3_SAT_TEMPERING = 2
Htg_3_MORNING_WARMUP = 3
Htg_3_TSTAT_HEATING = 4
Htg_3_UNOCC_HEATING = 5
Htg_3_OCC_HEATING = 6
Htg_3_OFF_DISABLED = 7
Htg_3_OFF_OAT_LOCKOUT = 8
Htg_3_OFF_SAT_LIMIT = 9
Htg_3_OFF_WAITING_FOR_CHANGEOVER = 10
Htg_3_COMFORT_VENTILATION = 11
*32578
ISO 10646
ASI X3.4
Micosoft DBCS Code
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool.
Note on B5: cedmonja: This point will occupy and unoccupy the unit.
Note on B6: Chad Edmondson: UCB OCC 24 VAC input status; Occupied indicates 24 VAC input to the OCC terminal, Unoccupied indicates 0 VAC input to the OCC terminal.
Note on B7: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B8: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B9: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B11: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B15: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B16: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B17: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B18: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B19: Chad Edmondson: By default "YES" the PID tuning parameters are managed by PRAC+(Pattern Recognition Adaptive Control) algorithm base on either Zone Temperature or Discharge Air Temperature process. PRAC+ can be turned off by changing the value of Cooling Adaptive Tuning Enable to "NO". Doing this will setup the PID to use the process defaults for either Zone Temperature or Discharge Temperature which can be found in the Cooling Adaptive Tuning chart attached to the right.
Note on B23: Chad Edmondson: Point is defaulted to "YES". This will prevent unit operation during unoccupied mode. Set to "NO" if you want to operate unit during unocc mode.
Note on B25: Chad Edmondson: SSE board is default to ISO 10646. Using another encoding type could prevent seeing bacnet point descriptions. You will need to change to the Encoding type your device is using.
Note on B29: cedmonja: Variable speed- Sets the SSE board to operate as a VAV unit and control fan speed according to static pressure. Fixed Variable-Sets the SSE board to operate according to a 8 fan speed selection when the blower is VFD controlled. Single Speed-Sets the SSE Board to operate according to 100% fan operation. With no VFD applied to RTU.
Note on B30: cedmonja: None-Sets board not to recognize APS if not being used. Variable-allows operation of APS applied to a SSE VAV setup.
Note on B32: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B43: cedmonja: Yes-Prevents blower operation request from the start of 1 stage heat commmand until a 24VAC input is recognized at the MV pin and the FanOnDlyHeat expires. No-Ignores this operation.
Note on B44: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B46: cedmonja: Yes-Permits continuous fan operation when in occupied mode. No-Only permits fan during a call for heat or cool.
Note on B55: Chad Edmondson: When RTU is a Heat pump the minimum stage setting is 2.
Note on B56: Chad Edmondson: Must equal number of cooling stages when applied to an RTU.
Note on B57: cedmonja: At the initiation of each cooling demand the compressor with the lowest run hours energizes first. The compressor with the next number of lowest run hours energizes next, and so on. At the termination of the cooling demand, the compressor with the most run hours stage off in reverse order.
Note on B58: cedmonja: If lead lag is enabled. Hot Gas Bypass will operate in this sequence if set to "YES". VAV operation: If compressor operation is ongoing and C1 is not running, and fan speed drops below 50%, compressors stage off and stage back on in order. If fan speed is greater than 50% and the SAT is less than 45°F, the Lead/Lag function disables. CV operation: If the SAT is less than 45°F, the Lead/Lag function disables.
Note on B60: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B61: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B62: cedmonja: If Cooling OAT Cutout Enble is Yes, the compressor is not permitted if the OAT is less than the cooling OAT Cutout. If Cooling OAT Cutout Enable is NO. the compressor cycles 10 minutes On and 5 minutes Off if the OAT is less than the LowAmb10On5Off Setpoint. If a compressor is in the 10 min On cycle and the evaportator temperature (EC1 thru EC4) drops below 26 degrees F. the compressor output de-endergizes and the 5 minute ASCD starts. After 5 minutes ASCD expires, the compressor ouput is permitted. Anytime the compressor output de-energizes due to the evaporator coil temperature protection it does not count towards a hard compressor lockout.
Note on B66: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B90: cedmonja: Setpoint does not allow heating operation when Operational OAT goes above the setpoint.
Note on B102: Chad Edmondson: 2-10VDC output status.
Note on B103: Chad Edmondson: sets action of 4-stage board modulating Htg 2-10 VDC output; No sets modulating Htg output at 2 VDC is 0%/closed and at 10 VDC is 100%/open. Yes sets modulating Htg output at 10 VDC is 0%/closed and at 2 VDC is 100%/open.
Note on B108: Chad Edmondson: Freezestat Alarm A freezestat must be field-supplied and field-installed. When 24 VAC is not present on terminal FSHW and: • the outdoor air temperature is greater than 40°F, no action is taken and the unit operates normally • the outdoor air temperature is 40° F or less, the hot water valve opens 100%, the indoor fan de-energizes, the economizer outside air damper is fully closed, and all other fans de-energize. • The control returns to normal if either: • 24 VAC is present on terminal FSHW, or • the outdoor air temperature rises above 40°F
Note on B109: Chad Edmondson: Staged- Set for gas or electric staged heating. Proportional- Set for modulating heating output 2-10VDC for hydronic or steam heat.
Note on B112: cedmonja: Yes-enables economizer function. No-disables economizer function. EconomizerFixed Variable Operation: When the control is in the occupied mode and the FAN output energizes and the VFD output reaches 100%, the Economizer Damper position is the Economizer Minimum Position Setpoint. When the VFD output reaches 50%, the Economizer Damper position is the Economizer Damper Minimum Position Low Speed Fan. When the VFD output is between 100% and 50%, the Economizer Damper is position proportionally between Economizer Minimum Position Setpoint and Economizer Damper Minimum Position Low Speed Fan. Note: To disable the VAV economizer minimum position reset, set the Economizer Minimum Position Setpoint and the Economizer Damper Minimum Position Low Speed Fan to the same value.
Note on B115: cedmonja: Value displays % economizer damper is open.
Note on B116: cedmonja: Economizer damper minimum % open setpoint during occupied mode.
Note on B117: cedmonja: Dry bulb economizer setpoint. When OAT drops below set point economizer functions starts.
Note on B118: cedmonja: Yes-Economizer free cooling is available. No-Economizer free cooling is not available.
Note on B119: cedmonja: Option A-(Do Not Use) Economizer damper position and/or time triggers compressor operation to supplement free cooling. Option B- Supply air temperature with VAV supply air temperature(upper/lower) setpoint triggers compressor operation to supplement free cooling.
Note on B120: cedmonja: Yes-Does not allow compressor operation during free cooling. No-allows compressor operation durig free cooling.
Note on B121: cedmonja: Single enthalpy free cooling setpoint. When Outside Air Enthalpy is below setpoint free cooling is available.
Note on B126: Chad Edmondson: Setpoint used to control SAT in economize setup set to Mechanical Option B CV Sensor. CV Option B Occupied With free cooling available and the operating space temperature is greater than the operating cooling setpoint, the dampers modulate to control the Upper SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes, then the dampers moduate to control to the Lower SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes and SAT is greater than the Lower SAT Setpoint +5°F, the first compressor output energizes. If the economizer position remains at 100% for another 5 minute time period, and the SAT is greater than the Lower SAT Setpoint +5°F, the second compressor output energizes. This process repeats every 5 minutes as long as the economizer position is at 100% until all the compressors energize. If the economizer position drops below 100% and does not reach minimum position, and returns to 100% and remains for 5-minutes, and the SAT is greater than the Lower SAT Setpoint +5°F, the next available compressor energizes and additional compressors energize until all the compressors energize. Any time the economizer remains at minimum position for 5 consecutive minutes, or SAT is lower than the Lower SAT Setpoint -5°F, the last energized compressor turns Off. If it remains at minimum position or SAT remains lower than the Lower SAT Setpoint -5°F, the compressors de-energize every 5 minutes until all are Off. If all compressor outputs de-engerize and the economizer modulates to control to Upper SAT Setpoint +/-0.5°F. When the cooling demand ends the compressors de-energize immediately and the dampers return to operating minimum position.
Note on B127: Chad Edmondson: Setpoint used to control SAT in economize setup set to Mechanical Option B CV Sensor. CV Option B Occupied With free cooling available and the operating space temperature is greater than the operating cooling setpoint, the dampers modulate to control the Upper SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes, then the dampers moduate to control to the Lower SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 5 consecutive minutes and SAT is greater than the Lower SAT Setpoint +5°F, the first compressor output energizes. If the economizer position remains at 100% for another 5 minute time period, and the SAT is greater than the Lower SAT Setpoint +5°F, the second compressor output energizes. This process repeats every 5 minutes as long as the economizer position is at 100% until all the compressors energize. If the economizer position drops below 100% and does not reach minimum position, and returns to 100% and remains for 5-minutes, and the SAT is greater than the Lower SAT Setpoint +5°F, the next available compressor energizes and additional compressors energize until all the compressors energize. Any time the economizer remains at minimum position for 5 consecutive minutes, or SAT is lower than the Lower SAT Setpoint -5°F, the last energized compressor turns Off. If it remains at minimum position or SAT remains lower than the Lower SAT Setpoint -5°F, the compressors de-energize every 5 minutes until all are Off. If all compressor outputs de-engerize and the economizer modulates to control to Upper SAT Setpoint +/-0.5°F. When the cooling demand ends the compressors de-energize immediately and the dampers return to operating minimum position.
Note on B128: Chad Edmondson: Operation details include: Economizer loading function works only when only one compressor is operating. If SAT is less than the SAT Low Limit Setpoint and the operating OAT is greater than 60°F, the economizer output increases to control the SAT to the Operating SAT Setpoint +/-0.5°F.
Note on B129: Chad Edmondson: California Title 24 fault detection requirement. Setting this point to off will eliminate the feedback alarm "Econ Not Modulating".
Note on B132: cedmonja: With the series 10 & 20 RTU the only curren option is Non-Modulating Power Exhaust.
Note on B144: cedmonja: Demand Ventilation mode selection. Disabled-No Demand Ventilation Function. Controlled by IAQ- Enables Demand Ventilation control with IAQ input. Differential between IAQ & OAQ- Enables Demand Ventilation control with a comparison between IAQ & OAQ.
Note on B148: cedmonja: IAQ sensor range.
Note on B155: cedmonja: This point will reflect the offset + or - range of the occupied heating setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B156: cedmonja: This point will reflect the offset + or - range of the occupied cooling setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B179: cedmonja: the source of the indoor air quality input in use; Local is from the economizer board IAQ 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates IAQ input is currently not present
Note on B180: cedmonja: The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present.
Note on B181: cedmonja: the source of the outdoor air quality input in use; Local is from economizer board OAQ 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
Note on B184: cedmonja: Operation: The Air Monitor Station will be wired to the JCI Economizer Module and accepts a 0-10VDC input at the FR ARI terminals. Below shows the wiring terminals and economizer module. The Fresh Air Max Sensor Range must match the range of the Air Monitoring Station on the unit. When the Fresh Air Intake value falls below the fresh air intake setpoint the economizer damper position increase above the minimum position until the fresh air intake value equals the fresh air intake setpoint +/- 40 CFM. When the fresh air intake value rises above the fresh air intake setpoint the economizer damper position decreases until the fresh air intake value equals the fresh air intake setpoint or it reaches Minimum position setpoint. Note: The low ambient minimum position may force the damper position below the current setpoint and disables the air monitoring station reset.
Note on B190: cedmonja: Normal Occupied Operation Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 output energizes and the AUX-HGR output energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 output energizes but the AUX-HGR output de-energizes. Any additional cooling demands energize compressor outputs, but do not change the status of the AUX-HGR output. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas
Note on B191: cedmonja: Alternate Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for both first and second cooling stages and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and C2 outputs energize and AUX-HGR de-energizes. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas Reheat Humidity Setpoint.
Note on B193: cedmonja: YES- Allows access to hot gas reheat moode selection in HGRAlt-En. NO-Does not allow access to hot gas reheat mode selection in HGRAlt-En.
Note on B194: cedmonja: YES- Allows hot gas reheat operation when occupancy status is Unoccupied. NO- Does not allow hot has reheat operation when occupancy status is Unoccupied.
Note on B199: cedmonja: The number of heat pump stages; 1 or more enabled the UCB H1 VAC output to position reversing valve, 2 ormore enabled the UCB H2 VAC output to initiate supplemental heat.
Note on B203: cedmonja: Cooling: Cooling calls are handled the same way as non-heat pump cooling units with one exception. Exception: During cooling, the control energizes the H1 output to turn on the Reversing Valve. The H1 output to the reversing valve remains energized between calls for cooling. If a heating call arises, the H1 output turns off. Heating: If a first stage of heating is called for (thermostat or zone sensor/network), all available compressors stage on, with a 30 second time delay between compressors. The Cooling Fan On Delay and Cooling Fan Off Delay are used for the first stage of heat pump heating. During a first stage of heating, the H1 output turns off and remain off between heat calls. If a second stage of heating is called for, the H2 or AUX output energizes the Emergency/Aux heating. If a thermostat calls for W2 only, only the H2 output energizes. The Heating Fan On Delay and Heating Fan Off Delay are used.

## RTU-Variable
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point/ *Enum drop down list | Type | Modbus Point | Read/Write | Settting value/ *drop down list
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level |  | Set at board level |  | 4 to 127
|  | OccMode | Commission>HVACZone>OccMode | 29518 | MV | 82 | Read/Write | External/ Schedule
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | MV | 84 | Read/Write | Occupied/ Unoccupied
|  | Occupancy Binary Input | Details>Service>Inputs>BinaryInputs>Occ | 29516 | MV | 291 | Read | Occupied/ Unoccupied
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | MV | Set at board level |  | "Yes" or "No"
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level |  | Set at board level |  | *Modbus Field Bus
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | MV | Set at board level |  | OFF
|  | Alarms | Alarms |  |  |  |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level |  | Set at board level |  | defaulted to 1
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level |  | Set at board level |  | Auto or 1200-76800
|  | Unit Name | Details>Unit>Name | Set at board level |  | Set at board level |  |  | Cooling Adaptive Tuning Default Parameters- Not Adjustable
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level |  | View at Board level |  | Current Version 3.0.0.1072 | Default Tuning Parameters
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level |  | Set at board level |  | "TRUE" or "FALSE" |  | Initial Prop Band | Intergral Time (sec)
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | MV | 292 | Read | Occupied/ Unoccupied | Zone- T | 4.2 | 892
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | AV | 80 | Read/Write | ON/OFF | DA-T | 21.8 | 203
|  | Self Test | Self Test>Start | Set at board Level |  | Set at board level |  | Start, Pause, Cancel, Status, Reset
|  | Cooling Adaptive Tuning Enabled | Details>Control>Clg>Setup>ClgAdapTunEn | 29882 | MV | 100 | Read/Write | "Yes" or "No"
|  | Heating Adaptive Tuning Enabled | Details>Control>Htg>Setup>HtgAdapTunEn | 29881 | MV | 114 | Read/Write | "Yes" or "No"
|  | Time | Update>Time | Set at Board Level |  | Set at board level |  | 24 hours Military Format
|  | Unit Status | Status>Unit-S | *29803 | MV | 280 | Read
|  | Off During Unoccuped Mode | Commision>HVACzone>OffDurUnocc | 29914 | MV | 88 | Read/Write | "Yes" or "No"
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>RTU | Set at board level |  |  |  | *RTU
|  | Bacnet Encoding Type | Controller>Network>EncodingType | *32578 | MV |  |  | 3.0.0.1116 Rev or higher
|  | Temporary Occupancy Timeout | Details>Zone>Indoor>TempOccTimeout | 29521 | AV | 85 | Read/Write | 30 to 120 min. time period
FAN SETUP/STATUS
|  | Fan Control | Summary>Fan>FanCtl-Type | 29555 | MV | Set at board level |  | Variable
|  | APS Setup | Details>Service>Factory>Standard>APS Setup | 29556 | MV | Set at board level |  | None or Variable
|  | APS Status | Details>Control>IndoorFan>Status>APS | 29557 | MV | 305 | Read | "ON" = APS closed
|  | Duct pressure Set Point | Details>Setpoints>DctPrs-Sp | 29566 | AV | 10 | Read/Write | 0-5"wc
|  | Duct pressure Shut down | Details>Control>IndoorFan>Setup>DctShutdownSp | 29568 | MV | 91 | Read/Write | 0-5"wc
|  | Net Override Fan Request | Details>Service>Inputs>NetworkInputs>NetFanReq | 29536 | MV | 87 | Read/Write | Writable Point to Force blower "ON"
|  | Fan Overload | Details>Control>IndoorFan>Setup>FanOvrload | 29553 | MV | 304 | Read
|  | Fan Status | Status>Fan-S | *29550 | MV | 302 | Read
|  | Fan VFD Status | Summary> Fan> FanVFD | 29551 | AV | 157 | Read
|  | Fan VFD Fault | Details>Control>IndoorFan>Status>FanVFDFlt | 29552 | MV | 303 | Read
|  | Fan "OFF" Start Heat | Details>Control>IndoorFan>Setup>FanoffStartHeat | 29569 | MV | 92 | Read/Write | "NO"
COOLING SETUP/STATUS
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | MV | 93 | Read/Write | "YES" or "NO"
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | AV | 263 | Read | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | AV | Set at board level |  | 1 to 4
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | AV | 32 | Read/Write | 1 to 4 Circuits
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | MV | 94 | Read/Write | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | AV | 21 | Read/Write | 0 to 100 degrees
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | MV | 98 | Read/Write | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | AV | 25 | Read/Write | 40 to 65 degrees
|  | Operating VAV Cooling Setpoint | Details>Setpoints>OprVAVClg-Sp | 29607 | AV | 160 | Read
|  | VAV Clg SA Upper Stpt | Details>Setpoints>SATUp-Sp | 29604 | AV | 26 | Read/Write | 60 degree
|  | VAV Clg SA Lower Stpt | Details>Setpoints>SATLo-Sp | 29605 | AV | 27 | Read/Write | 55 degree
|  | VAV SA Reset Stpt | Details>Setpoits>SATRst-Sp | 29606 | AV | 28 | Read/Write | 72 degree
|  | VAV Operating Cooling Supply Air Temp Set point | Details>Setpoints>OprVAVClg-Sp | 29607 | AV | 160 | Read
|  | Cooling Status | Status>Clg-S | *29577 | MV | 308 | Read | Displays Cooling Status
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | MV | Set at board level |  | "YES" or "NO"
|  | Hot Gas Bypass Installed (Present) | Details>Service>Factory>Standard>HGP-Inst | 29623 | MV | Set at board level |  | "YES" or "NO"
HEATING SETUP/STATUS
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | MV | 105 | Read/Write | "YES" or "NO"
|  | Heating Status | Status>Htg-S | *29708 | MV | 347 | Read
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | AV | 264 | Read | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | AV | Set at board level |  | 1 to 3
|  | Heating OAT Cutout Setpoint | Details>Control>Htg>Setup>HtgOATCutout-Sp | 29711 | AV | 38 | Read/Write | 0 to 100 degrees
|  | Morning Warm Up Enabled | Details>Control>Htg>Setup>MornW-En | 29822 | MV | 109 | Read/Write | "ON" if MornW used
|  | Morning Warm Up Stpt | Details>Control>Htg>Setup>MornWRAT-Sp | 29823 | AV | 41 | Read/Write | 50 to 85 degrees
|  | VAV Occupied Heat | Details>Setpoints>HtgOcc-En | 29722 | MV | 107 | Read/Write | "YES" or "NO"
|  | VAV Occupied Heat Stpt | Details>Setpoints>VAVHtgOcc-Sp | 29723 | AV | 39 | Read/Write | 40 to 85 degrees
|  | VAV Operating Heat Stpt | Details>Setpoints>VAVOprHtg-Sp | 29726 | AV | 250 | Read | Displays set point
|  | VAV Unccupied Heat Stpt | Details>Setpoint>VAVHtgUnocc-Sp | 29725 | AV | 40 | Read/Write | 45 to 98 degress
|  | VAV Unccupied Heat Enable | Details>Setpoint>HtgUnocc-En | 29724 | MV | 108 | Read/Write | "Yes" or "No"
|  | Supply Air Heating Limit Enabled | Detals>Control>Htg>Setup>SATHtgLimit-En | 29709 | MV | 106 | Read/Write | "YES" or "NO"
|  | Supply Air Heating Limit Set point | Details>Control>Htg>Setup>SATHtgLimt-Sp | 29710 | AV | 37 | Read/Write | 100 degree to 180 degree
|  | Hot Water Heat Valve % Output (4 stage Exp Board) | Details>Control>Htg>Status>HWV | 29741 | AV | 252 | Read | 0 to 100%
|  | Hot Water Valve Rev Acting (4 stage Exp. Board) | Details>Control>Htg>Setup>HydReverse | 29742 | MV | 115 | Read/Write | "YES" or "NO"
|  | Hot Water Htg Stage 1 SAT Sp (4 stage Exp. Board) | Details>Control>Htg>Setup>HydH1SA-Sp | 29743 | AV | 51 | Read/Write | 80 to 180 degrees
|  | Hot Water Htg Stage 2 SAT Sp ( 4 stage Exp. Board) | Details>Control>Htg>Setup>HydH2SA-Sp | 29744 | AV | 52 | Read/Write | 80 to 180 degrees
|  | Hot Water Heat SAT Tempering Enabled (4 stage Exp. Board) | Details>Control>Htg>SATTempHydHt-En | 29745 | MV | 116 | Read/Write | "Yes" or "No"
|  | Hot Water Heat SAT Tempering Set Point (4 stage Exp. Board) | Commission>Htg>SATTempHydHt-Sp | 29746 | AV | 53 | Read/Write
|  | Hot Water Freeze Stat (4 stage Exp. Board) | Details>Service>Inputs>BinaryInputs>Limit>FSHW | 29712 | MV | 348 | Read | Normal or Alarm
|  | Heating Control Type | Details>Control>Htg>Status>Htg-Type | Set at board Level |  | Set at board level |  | Staged or Proportional
ECONOMIZER SETUP/STATUS
|  | Economizer Enabled | Commission>Econ>Econ-En | 29747 | MV | 118 | Read/Write | "YES" or "NO"
|  | Economizer Status | Status>Econ-S | *29750 | MV | 370 | Read
|  | Economizer Firware | Controller>SysCntrls>Econ>EconMainVer | N/A |  | N/A |  | View at board level or Map Gateway
|  | Economizer Damper Position | Details>Service>Inputs>Sensors>EconDampPos | 29748 | AV | 253 | Read | % open
|  | Economizer Minimum Position | Details>Control>Econ>Setup>Econ-MinPos | 29759 | AV | 77 | Read/Write | % Open Set point
|  | Economizer OAT Set point | Details>Control>Econ>Setup>EconOAT-SpEn | 29753 | AV | 55 | Read/Write | 40 to 80 degrees
|  | Economizer Free Cooling Available | Summary>Econ>Econ-Free | 29749 | MV | 369 | Read | "YES" or "NO"
|  | Economizer Mechanical Setup | Details>Control>Econ>Setup>EconMechStp | 29912 | MV | Set at board level |  | Option B
|  | All Compressor OFF-Economizer | Details>Control>Clg>Setup>AllCompOff-Econ | 29584 | MV | 96 | Read/Write | "YES" or "NO"
|  | Econ OA Enthalpy Setpoint | Details>Control>Econ>Setup>EconOAEth-Sp | 29754 | AV | 56 | Read/Write | 10 to 50 BTU/Lb
|  | Free Cooling Selection | Details>Control>Econ>Setup>FreeClg-Sel | 29752 | MV | 119 | Read/Write | * Auto
|  | Economizer Loading Enabled | Details>Control>Clg>Setup>EconLoad-En | 29583 | MV | 95 | Read/Write | "YES" or "NO"
|  | Economzer Fault Detection Enable | Commission>Econ>EconFltDetectEn | 29915 | MV | 132 | Read/Write | Disable/Enable
Power Exhaust Setup/STATUS
|  | Power Exhaust Fan Type | Details>Service>Factory>Econ>ExFType | 29774 |  | set at board level |  | *None
|  | Power Exhaust Fan Command | Details>Control>PowerEx>Status> | 29775 | MV | 376 | Read
|  | Power Exhaust Fan Status | Details>Control>PowerEx>Status>ExFan | *29777 | MV | 377 | Read
|  | Power Exhaust Modulating Damper Output | Summary>PowerEx>EAD-O | 29782 | AV | 261 | Read
|  | Building Pressure Set Point | Summary>PowerEx>Bldg-Sp | 29780 | AV | 63 | Read/Write
|  | Econ Damper Position Power Exhaust "OFF" | Summary>PowerEx>EconDmpPosFanOff | 29786 | AV | 67 | Read/Write
|  | Econ Damper Position Power Exhaust "ON" | Summary>PowerEx>EconDmpPosFanOn | 29785 | AV | 66 | Read/Write
|  | Power Exhaust Damper Position "OFF" | Commission>PoweEx>ExDmpPosFanOff | 29784 | AV | 65 | Read/Write
|  | Power Exhaust Damper Position "On" | Commission>PoweEx>ExDmpPosFanOn | 29783 | AV | 64 | Read/Write
|  | Power Exhaust VFD Output Status | Summary>PowerEx>ExFanVFD | 29776 | AV | 258 | Read
CO2 Demand Ventilation Setup/STATUS
|  | (CO2) Demand Ventilation Mode | Commission>Dvent>Dvent-Mode | 29765 | MV | 120 | Read/Write | *Disabled
|  | (CO2) Demand Ventilation Mode IAQ Set Point | Commission>Dvent>DventIAQ-Sp | 29767 | AV | 61 | Read/Write | 0 to 5000 ppm
|  | (CO2) Demand Ventilation Max Econ Damper Position | Commission>Dvent>DVentMaxEconPos | 29766 | AV | 60 | Read/Write | range 0% to 100% open
|  | (CO2) OAQ Range | Commission>Dvent>OAQRange | 29548 | MV | 301 | Read | 0 ppm to 5000 ppm
|  | (CO2) IAQ Range | Commission>Dvent>IAQRange | 29529 | AV | 294 | Read | 0 ppm to 5000 ppm
|  | (CO2) Demand Ventilation Differential Set Point | Commission>Dvent>DVentDiff-Sp | 29768 | AV | 62 | Read/Write | 0 ppm to 5000 ppm
Sensor Inputs & Readings
|  | Supply Air Temperature | Details>Service>Inputs>Sensors>SAT | 29564 | AV | 158 | Read
|  | Return Air Temperature | Details>Service>Inputs>Sensors>RAT | 29764 | AV | 139 | Read
|  | Operational Outdoor Air Temperature | Details>Zone>Outdoor>OprOAT | 29541 | AV | 153 | Read
|  | Operational Space Temperature | Details>Zone>Indoor>OprST | 29522 | AV | 135 | Read
|  | Operational Space Sensor Offset | Details>Zone>Indoor>OprSSO | 29537 | AV | 140 | Read
|  | Space Temperature Source | Details>Zone>Indoor>STsrc | 29523 | MV | 293 | Read | *Return Air Temp
|  | Space Sensor Offset Range | Details>Zone>Indoor>SSORange | N/A |  | N/A |  | 0 to 5 degrees F setpoint
|  | Space sensor Offset Source | Details>zone>Indoor>SSOSrc | 29538 | MV | 298 | Read
|  | Space Humidity RAH input | Details>Control>Econ>Status>RAH | 29828 | AV | 138 | Read
|  | Outdoor Air Humidity Input | Details>Service>Inputs>Sensor>OAH | N/A |  | N/A
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531 | AV | 137 | Read
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OA-Enth | 29545 | AV | 155 | Read
|  | Return Air Enthalpy | Details>Control>Econ>Status>RA-Enth | 29763 | AV | 257 | Read
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531 | AV | 137 | Read
|  | Operational Outdoor Air Humidity | Details>Control>Econ>Status>OprOAH | 29544 | AV | 154 | Read
|  | Net Override Space Temperature | Details>Service>Inputs>NetworkInputs>NetST | 29526 | AV | 1 | Read/Write | Writable Point to Space Temp
|  | Net Override Outdoor Air Temperature | Details>Service>Inputs>NetworkInputs>NetOAT | 29543 | AV | 6 | Read/Write | Writable Point to OAT
|  | Net Override Indoor Air Quality | Details>Service>Inputs>NetworkInputs>NetIAQ | 29530 | AV | 3 | Read/Write | Writable Point to IAQ
|  | Net Override Outdoor Air Quality | Details>Service>Inputs>NetworkInputs>NetOAQ | 29549 | AV | 8 | Read/Write | Writable Point to OAQ
|  | Net Override Outdoor Air Humidity | Details>Service>Inputs>NetworkInputs>NetOAH | 29546 | AV | 7 | Read/Write | Writable Point to OAH
|  | Net Override Space Humidity | Details>Service>Inputs>NetworkInputs>NetSH | 29533 | AV | 4 | Read/Write | Writable Point to Space Humidity
|  | Net Override Space Sensor Offset | Details>Service>Inputs>NetworkInputs>NetSSO | 29540 | AV | 5 | Read/Write | Writable Point to Space Sensor offset
|  | Building Pressure | Summary>PowerEx>BldgPres | 29781 | AV | 260 | Read | (-).25 to .25"wc
|  | Duct Pressure | Summary>Fan>DctPrs | 29565 | MV | 159 | Read | 0-5" wc
|  | (CO2) IAQ Input | Details>Service>Inputs>Sensor>IAQ | N/A |  | N/A
|  | (CO2) OAQ Input | Details>Service>Inputs>Sensor>OAQ | N/A |  | N/A
|  | Operational IAQ | Summary>Dvent>OprIAQ | 29527 | AV | 136 | Read
|  | IAQ source | Details>Zone>Indoor>IAQsrc | 29528 | MV | 294 | Read
|  | Operational OAQ | Summary>Dvent>OprOAQ | 29547 | AV | 156 | Read
|  | OAQ source | Deatails>Zone>Outdoor>OAQsrc | 29548 | MV | 301 | Read
AIR MONITOR
|  | Fresh Air Enable | Details>Control>AirMonStation>FRSHAIR-EN | Set at board Level |  | Set at board level |  | Enable/Disable
|  | Fresh Air Flow Reading | Details>Control>AirMonStation>FR-Air | 29796 | AV | 262 | Read | CFM reading
|  | Air Monitor Flow Range | Details>Control>AirMonStation>MOA-Range | 29797 | AV | 70 | Read/Write | Range 0 to 50000 CFM
|  | Air Monitor Flow Setpoint | Details>Control>AirMonStation>MOAflow-Sp | 29795 | AV | 69 | Read/Write | Range 0 to 50000 CFM
HOT GAS REHEAT
|  | Hot Gas Reheat Enabled for Operation | Details>Service>Factory>Standard>HGR-En | 29789 | MV | 123 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Alternate Operation Enabled | Details>Control>HGR>HGRAlt-En | 29793 | MV | 124 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Gas Reheat Humidity Setpoint | Details>Control>HGR>HGRHum-SP | 29792 | AV | 68 | Read/Write | 0% to 100%
|  | Hot Gas Reheat Alternate Operation Writable | Details>Control>HGR>HGRAltWrite | 29794 |  | N/A | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Enabled for Unoccupied Operation | Details>Control>HGR>HGRUnocc-En | 29904 | MV | 133 | Read/Write | "YES" or "NO"
|  | Hot Gas Reheat Unoccupied Humidity Setpoint | Details>Control>HGR>HGRUnoccHum-Sp | 29903 | AV | 78 | Read/Write | 0% to 100%
|  | Hot Gas Reheat Status | Details>Control>HGR>HGR-S | *29791 | MV | 380 | Read
HEAT PUMP |  | (Note: # of Heating and Cooling Stages will have to be adjusted appropriately for Heat Pump Operation)
|  | Heat Pump number of Stages | Details>Service>Factory>Standard>#HtPumpStgs | 29898 | AV | Set at board level |  | 1 to 2 stages
|  | Defrost Curve Set | Commission>Defrost>DefrostCurveSel | 29899 (Defrost State) | MV | 177 | Read/Write | Curve Selection 1 through 6
|  | Reversing Valve | Summary>HeatPump>RevVlv | 29900 |  | 366 | Read | Output Status
|  | Auxillary Heat | Summary>HeatPump>AuxHtg | 29901 |  | 367 | Read | Output Status
|  | Heat Pump Mode | Summary>HeatPump>Mode | 29902 |  | 368 | Read | Operating Status
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | AV | 32 | Read/Write
*29550
[12 empty] | FAN_OFF_IDLE = 0 | *Wired Field Bus = BACnet MSTP
[12 empty] | FAN_ON_PURGE = 1 | *N2 Slave Field Bus
[12 empty] | FAN_ON_GAS_VALVE = 2 | *Modbus Field Bus
FAN_ON_DEFROST = 3
[12 empty] | FAN_ON_THERMOSTAT_REQST = 4 | *Start
[12 empty] | FAN_ON_FAN_OFF_DELAY_COOL = 5 | *Pause
[12 empty] | FAN_ON_FAN_OFF_DELAY_HEAT = 6 | *Cancel
[12 empty] | FAN_ON_CONTINUOUS_FAN_OCC_OP = 7 | *Status
[12 empty] | FAN_ON_NORMAL_COMMAND = 8 | *Reset
FAN_OFF_EXCEEDING_DUCT_PRESSURE = 9
[12 empty] | FAN_OFF_LOW_VOLTAGE = 10 | *Split
[12 empty] | FAN_OFF_FAN_OVERLOAD_LOCKOUT = 11 | *RTU
[12 empty] | FAN_OFF_FAN_VFD_FAULT = 12 | *Heat Pump
[12 empty] | FAN_OFF_HOT_WATER_FREEZE_STAT = 13 | *Unknown
FAN_OFF_AIR_PROVING_SWITCH = 14
[12 empty] | FAN_OFF_MIN_OFF_DELAY = 15 | * Auto
[12 empty] | FAN_OFF_FAN_ON_DELAY_HEAT = 16 | * Dry Bulb
[12 empty] | FAN_OFF_FAN_ON_DELAY_COOL = 17 | * Single Enthalpy
* Dual Enthalpy
[12 empty] | *29577 | *None
[12 empty] | COOL_OFF_IDLE = 0 | *Non-Modulating
[12 empty] | COOL_THERM_COOLING = 1 | *Modulating Damper
[12 empty] | COOL_UNOCC_COOLING = 2 | *Variable Frequency Fan
COOL_OCC_COOLING = 3
[12 empty] | COOL_OFF_OAT_LOCKOUT = 4 | *Off-Idle
[12 empty] | COOL_OFF_DISABLED = 5 | *On-Normal Command
[12 empty] | COOL_OFF_LOCKOUT= 6 | *Off-Disabled
[12 empty] | COOL_OFF_LOW_SUPPLY_VOLT = 7 | *Off-VFD Fault
[12 empty] | COOL_OFF_LOW_AMBIENT = 8 | *Off-Low Building Static Pressure
[12 empty] | COOL_OFF_LOW_AMBIENT_PRE_RUN_DELAY = 9 | *Off-Economizer Damper Position
COOL_OFF_WAITING_CHANGEOVER 10
[12 empty] | COOL_OFF_FREE_COOLING 11 | *Disabled
[12 empty] | COOL_COMFORT_VENT 12 | *Controlled by IAQ
*Diff. Between IAQ & OAQ
*29615
[12 empty] | CLG_1_OFF_IDLE = 0 | *Unreliable
[12 empty] | CLG_1_ON_MIN_ON_TIME = 1 | *Return Air Temp
[12 empty] | CLG_1_ON_NORMAL_CMD = 2 | *Local Input
[12 empty] | CLG_1_OFF_CLG_DISABLED = 3 | *Network Sensor
[12 empty] | CLG_1_OFF_OAT_CUTOUT = 4 | *BAS Override
[12 empty] | CLG_1_OFF_LOW_AMBIENT_TEMP = 5 | *Not Available
CLG_1_OFF_LOW_SUPPLY_VOLT = 6
CLG_1_OFF_HIGH_PRESSURE_LOCK = 7
CLG_1_OFF_LOW_PRESSURE_LOCK = 8
CLG_1_OFF_FREEZE_CONDITION = 9
CLG_1_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_1_OFF_COOLING_STAGE_DISABLED = 11
*29616
CLG_2_OFF_IDLE = 0
CLG_2_ON_MIN_ON_TIME = 1
CLG_2_ON_NORMAL_CMD =2
CLG_2_OFF_CLG_DISABLED = 3
CLG_2_OFF_OAT_CUTOUT = 4
CLG_2_OFF_LOW_AMBIENT_TEMP = 5
CLG_2_OFF_LOW_SUPPLY_VOLT = 6
CLG_2_OFF_HIGH_PRESSURE_LOCK = 7
CLG_2_OFF_LOW_PRESSURE_LOCK = 8
CLG_2_OFF_FREEZE_CONDITION = 9
CLG_2_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_2_OFF_COOLING_STAGE_DISABLED = 11
*29617
CLG_3_OFF_IDLE = 0
CLG_3_ON_MIN_ON_TIME = 1
CLG_3_ON_NORMAL_CMD = 2
CLG_3_OFF_CLG_DISABLED = 3
CLG_3_OFF_OAT_CUTOUT = 4
CLG_3_OFF_LOW_AMBIENT_TEMP = 5
CLG_3_OFF_LOW_SUPPLY_VOLT = 6
CLG_3_OFF_HIGH_PRESSURE_LOCK = 7
CLG_3_OFF_LOW_PRESSURE_LOCK = 8
CLG_3_OFF_FREEZE_CONDITION = 9
CLG_3_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_3_OFF_COOLING_STAGE_DISABLED = 11
*29618
CLG_4_OFF_IDLE = 0
CLG_4_ON_MIN_ON_TIME = 1
CLG_4_ON_NORMAL_CMD = 2
CLG_4_OFF_CLG_DISABLED = 3
CLG_4_OFF_OAT_CUTOUT = 4
CLG_4_OFF_LOW_AMBIENT_TEMP = 5
CLG_4_OFF_LOW_SUPPLY_VOLT = 6
CLG_4_OFF_HIGH_PRESSURE_LOCK = 7
CLG_4_OFF_LOW_PRESSURE_LOCK = 8
CLG_4_OFF_FREEZE_CONDITION = 9
CLG_4_OFF_ANTI_SHORT_CYCLE_DELAY = 10
CLG_4_OFF_COOLING_STAGE_DISABLED = 11
*29803
UNIT_IDLE = 0
UNIT_SD_ALARM = 1
UNIT_PURGE_COMMAND = 2
UNIT_SELF_TEST = 3
UNIT_MORNING_WARM_UP= 4
UNIT_AIR_TEMPERING = 5
UNIT_DEHUMIDIFICATION = 6
UNIT_HEATING = 7
UNIT_COOLING = 8
UNIT_ECONOMIZER = 9
UNIT_FAN_ONLY = 10
UNIT_COMFORT_VENTILATION = 11
*29708
HEAT_OFF_IDLE = 0
HEAT_ON_DEFROST = 1
HEAT_SAT_TEMPERING = 2
HEAT_MORNING_WARMUP = 3
HEAT_TSTAT_HEATING = 4
HEAT_UNOCC_HEATING = 5
HEAT_OCC_HEATING = 6
HEAT_OFF_DISABLED = 7
HEAT_OFF_OAT_LOCKOUT = 8
HEAT_OFF_SAT_LIMIT = 9
HEAT_OFF_WAITING_FOR_CHANGEOVER = 10
HEAT_COMFORT_VENTILATION = 11
*29750
ECONOMIZER_DISABLED = 0
ECONOMIZER_DAMPER_NOT_FUNCTIONAL = 1
ECONOMIZER_PURGE = 2
ECONOMIZER_UNAVAIL_SENSOR_FAULT = 3
ECONOMIZER_ECON_LOADING = 4
ECONOMIZER_SAT_HIGH_LIMIT = 5
ECONOMIZER_MIXED_AIR_LL = 6
ECONOMIZER_DEMAND_VENT_AIR_QUALITY = 7
ECONOMIZER_OUTDOOR_AIRFLOW_CNTL = 8
ECONOMIZER_FREE_CLG_IS_AVAIL = 9
ECONOMIZER_MIN_POSITION = 10
ECONOMIZER_TEST = 11
ECONOMIZER_COMFORT_VENTILATION = 12
ECONOMIZER_LOW_OA_AMBIENT = 13
*29777
EXHAUST_FAN_OFF_IDLE = 0
EXHAUST_FAN_ON_NORMAL_COMMAND = 1
EXHAUST_FAN_OFF_DISABLED = 2
EXHAUST_FAN_OFF_VFD_FAULT = 3
EXHAUST_FAN_OFF_LOW_BLDG_STATIC_PRESSURE = 4
EXHAUST_FAN_OFF_ECON_DAMPTER_POS = 5
*29791
HOT_GAS_OFF_IDLE = 0
HOT_GAS_ON_NORMAL_COMMAND = 1
HOT_GAS_ON_ALT_OPERATION_CMD = 2
HOT_GAS_OFF_DISABLED = 3
*32578
ISO 10646
ASI X3.4
Micosoft DBCS Code
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool.
Note on B5: cedmonja: This point will occupy and unoccupy the unit.
Note on B6: Chad Edmondson: UCB OCC 24 VAC input status; Occupied indicates 24 VAC input to the OCC terminal, Unoccupied indicates 0 VAC input to the OCC terminal.
Note on B7: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B8: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B9: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B11: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B15: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B16: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B17: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B18: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B19: Chad Edmondson: By default "YES" the PID tuning parameters are managed by PRAC+(Pattern Recognition Adaptive Control) algorithm base on either Zone Temperature or Discharge Air Temperature process. PRAC+ can be turned off by changing the value of Cooling Adaptive Tuning Enable to "NO". Doing this will setup the PID to use the process defaults for either Zone Temperature or Discharge Temperature which can be found in the Cooling Adaptive Tuning chart attached to the right.
Note on B23: Chad Edmondson: Point is defaulted to "YES". This will prevent unit operation during unoccupied mode. Set to "NO" if you want to operate unit during unocc mode.
Note on B25: Chad Edmondson: SSE board is default to ISO 10646. Using another encoding type could prevent seeing bacnet point descriptions. You will need to change to the Encoding type your device is using.
Note on B29: cedmonja: Variable speed- Sets the SSE board to operate as a VAV unit and control fan speed according to static pressure. Fixed Variable-Sets the SSE board to operate according to a 7 fan speed selection when the blower is VFD controlled. Single Speed-Sets the SSE Board to operate according to 100% fan operation. With no VFD applied to RTU.
Note on B30: cedmonja: None-Sets board not to recognize APS if not being used. Variable-allows operation of APS applied to a SSE VAV setup.
Note on B34: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B39: cedmonja: Yes-Prevents blower operation request from the start of 1 stage heat commmand until a 24VAC input is recognized at the MV pin and the FanOnDlyHeat expires. No-Ignores this operation. Note: When board is set to variable operation. This point is only visable when fan control type is set to Fixed Variable or Single Speed. You must set the point to "No" in Variable operation if you do not want the fan to shutdown according to timers.
Note on B42: cedmonja: VAV Cooling Operation: If the operational space temperature rises + 2°F or more above the VAV Cooling Supply Air Temperature Reset Setpoint, the VAV Cooling Supply Air Temp Lower Setpoint is used for the Operational VAV Cooling Setpoint. If the operational space temperature falls below the Supply Air Temperature Reset Setpoint the Supply Air Temperature Upper Setpoint is used for the Operational VAV Cooling Setpoint.
Note on B45: Chad Edmondson: Must equal number of cooling stages when applied to an RTU.
Note on B46: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B47: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B48: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B50: cedmonja: The VAV cooling SAT setpoint in use; with OprST above SATRst-Sp is SATLo-Sp, with OprST below SATRst-Sp is SATUp-Sp; cooling operation requests are initiated when OprST rises above this setpoint.
Note on B56: cedmonja: At the initiation of each cooling demand the compressor with the lowest run hours energizes first. The compressor with the next number of lowest run hours energizes next, and so on. At the termination of the cooling demand, the compressor with the most run hours stage off in reverse order.
Note on B57: cedmonja: If lead lag is enabled. Hot Gas Bypass will operate in this sequence if set to "YES". VAV operation: If compressor operation is ongoing and C1 is not running, and fan speed drops below 50%, compressors stage off and stage back on in order. If fan speed is greater than 50% and the SAT is less than 45°F, the Lead/Lag function disables. CV operation: If the SAT is less than 45°F, the Lead/Lag function disables.
Note on B65: cedmonja: Setpoint does not allow heating operation when Operational OAT goes above the setpoint.
Note on B66: cedmonja: With a BI occupied command the supply fan turns on for a five minute stabilization period and then operating space temperature is compared to morning warm-up return air temp setpoint. If the value is equal to or below the morning warm-up return air temp setpoint, all heat stages operate for at least 5 minutes. If the value is above the morning warmup return air temp setpoint, the control goes into Occupied mode.
Note on B68: cedmonja: VAV Heat Operation: The control must be in an occupied mode and not in morning warm-up mode. If the operational space temperature drops lower than the VAV Occupied Heating Setpoint, all cooling stages de-energize after all compressor minimum runtimes have expired and after the two minute cool to heat changeover delay has expired, all heat stages energize with approximately 30 seconds delay between stages. Heat remains energized until the operational space temperature reaches the VAV Occupied Heating Setpoint + 1°F. Any time the control enters the heat mode, VAV BOX contact closes. Warning: If the unit is in a heating mode, the control continues to vary the DC output to control duct pressure to the Duct Static Pressure setpoint. Therefore, in any VAV heating mode, all VAV boxes must be commanded open far enough to get adequate airflow to support the heating function and to prevent the heat section high temperature limit switches from opening.
Note on B72: cedmonja: VAV Unoccupied Heat Operation: YES- Allow VAV heating in unoccupied operation. NO-Does not allow VAV heating in unoccupied operation. Control must be in an unoccupied mode and not in morning warm-up mode. If the operational space temperature drops lower than the VAV Heating Unoccupied Setpoint all heat stages energize with approximately 30 seconds delay between stages. Heat remains energized until the operational space temperature reaches the VAV Heating Unoccupied Setpoint + 3°F. Any time the control enters the heat mode, VAV box contact closes. Warning: If the unit is in a heating mode, the control continues to vary the DC output to control duct pressure to the Duct Static Pressure setpoint. Therefore, in any VAV heating mode, all VAV boxes must be commanded open far enough to get adequate airflow to support the heating function and to prevent the heat section high temperature limit switches from opening.
Note on B75: Chad Edmondson: 2-10VDC output status.
Note on B76: Chad Edmondson: sets action of 4-stage board modulating Htg 2-10 VDC output; No sets modulating Htg output at 2 VDC is 0%/closed and at 10 VDC is 100%/open. Yes sets modulating Htg output at 10 VDC is 0%/closed and at 2 VDC is 100%/open.
Note on B81: Chad Edmondson: Freezestat Alarm A freezestat must be field-supplied and field-installed. When 24 VAC is not present on terminal FSHW and: • the outdoor air temperature is greater than 40°F, no action is taken and the unit operates normally • the outdoor air temperature is 40° F or less, the hot water valve opens 100%, the indoor fan de-energizes, the economizer outside air damper is fully closed, and all other fans de-energize. • The control returns to normal if either: • 24 VAC is present on terminal FSHW, or • the outdoor air temperature rises above 40°F
Note on B82: Chad Edmondson: Staged- Set for gas or electric staged heating. Proportional- Set for modulating heating output 2-10VDC for hydronic or steam heat.
Note on B85: cedmonja: Yes-enables economizer function. No-disables economizer function.
Note on B88: cedmonja: Value displays % economizer damper is open.
Note on B89: cedmonja: Economizer damper minimum % open setpoint during occupied mode.
Note on B90: cedmonja: Dry bulb economizer setpoint. When OAT drops below set point economizer functions starts.
Note on B91: cedmonja: Yes-Economizer free cooling is available. No-Economizer free cooling is not available.
Note on B92: cedmonja: Option A-(Do Not Use) Economizer damper position and/or time triggers compressor operation to supplement free cooling. VAV Unit Sensor Option B With free cooling available and the SAT is greater than the operating VAV SAT Setpoint, the dampers modulate to control the operating VAV SAT Setpoint +/-0.5°F. If the economizer position remains at 100% for 10 consecutive minutes and SAT is greater than the operating VAV SAT Setpoint +5°F, the first compressor output energizes. If the economizer position remains at 100% for another 5 minute time period, and the SAT is greater than the operating VAV SAT Setpoint +5°F, the second compressor output energizes. This process repeats every 5 minutes as long as the economizer position is at 100% until all the compressors energize. If the economizer position drops below 100% and does not reach minimum position, and returns to 100% and remains for 5-minutes, and the SAT is greater than the operating VAV SAT Setpoint +5°F, the next available compressor energizes and additional compressors energize until all the compressors energize. Any time the economizer remains at minimum position for 5 consecutive minutes, or SAT is lower than the operating VAV SAT Setpoint -5°F, the last energized compressor turns Off. If it remains at minimum position or SAT remains lower than the operating VAV SAT Setpoint -5°F, the compressors de-energize every 5 minutes until all are Off. If all compressor outputs de-engerize and the economizer modulates to control to operating VAV SAT Setpoint +/-0.5°F. When the cooling demand ends the compressors de-energize immediately and the dampers return to operating minimum position.
Note on B93: cedmonja: Yes-Does not allow compressor operation during free cooling. No-allows compressor operation durig free cooling.
Note on B94: cedmonja: Single enthalpy free cooling setpoint. When Outside Air Enthalpy is below setpoint free cooling is available.
Note on B96: Chad Edmondson: Operation details include: Economizer loading function works only when only one compressor is operating. If SAT is less than the SAT Low Limit Setpoint and the operating OAT is greater than 60°F, the economizer output increases to control the SAT to the Operating SAT Setpoint +/-0.5°F.
Note on B97: Chad Edmondson: California Title 24 fault detection requirement. Setting this point to off will eliminate the feedback alarm "Econ Not Modulating".
Note on B100: cedmonja: With the series 10 & 20 RTU the only curren option is Non-Modulating Power Exhaust.
Note on B112: cedmonja: Demand Ventilation mode selection. Disabled-No Demand Ventilation Function. Controlled by IAQ- Enables Demand Ventilation control with IAQ input. Differential between IAQ & OAQ- Enables Demand Ventilation control with a comparison between IAQ & OAQ.
Note on B116: cedmonja: IAQ sensor range.
Note on B147: cedmonja: the source of the indoor air quality input in use; Local is from the economizer board IAQ 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates IAQ input is currently not present
Note on B148: cedmonja: The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present.
Note on B149: cedmonja: the source of the outdoor air quality input in use; Local is from economizer board OAQ 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
Note on B152: cedmonja: Operation: The Air Monitor Station will be wired to the JCI Economizer Module and accepts a 0-10VDC input at the FR ARI terminals. Below shows the wiring terminals and economizer module. The Fresh Air Max Sensor Range must match the range of the Air Monitoring Station on the unit. When the Fresh Air Intake value falls below the fresh air intake setpoint the economizer damper position increase above the minimum position until the fresh air intake value equals the fresh air intake setpoint +/- 40 CFM. When the fresh air intake value rises above the fresh air intake setpoint the economizer damper position decreases until the fresh air intake value equals the fresh air intake setpoint or it reaches Minimum position setpoint. Note: The low ambient minimum position may force the damper position below the current setpoint and disables the air monitoring station reset.
Note on B158: cedmonja: Normal Occupied Operation Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 output energizes and the AUX-HGR output energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 output energizes but the AUX-HGR output de-energizes. Any additional cooling demands energize compressor outputs, but do not change the status of the AUX-HGR output. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas
Note on B159: cedmonja: Alternate Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for both first and second cooling stages and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and C2 outputs energize and AUX-HGR de-energizes. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas Reheat Humidity Setpoint.
Note on B161: cedmonja: YES- Allows access to hot gas reheat moode selection in HGRAlt-En. NO-Does not allow access to hot gas reheat mode selection in HGRAlt-En.
Note on B162: cedmonja: YES- Allows hot gas reheat operation when occupancy status is Unoccupied. NO- Does not allow hot has reheat operation when occupancy status is Unoccupied.
Note on B167: cedmonja: The number of heat pump stages; 1 or more enabled the UCB H1 VAC output to position reversing valve, 2 ormore enabled the UCB H2 VAC output to initiate supplemental heat.
Note on B171: cedmonja: Cooling: Cooling calls are handled the same way as non-heat pump cooling units with one exception. Exception: During cooling, the control energizes the H1 output to turn on the Reversing Valve. The H1 output to the reversing valve remains energized between calls for cooling. If a heating call arises, the H1 output turns off. Heating: If a first stage of heating is called for (thermostat or zone sensor/network), all available compressors stage on, with a 30 second time delay between compressors. The Cooling Fan On Delay and Cooling Fan Off Delay are used for the first stage of heat pump heating. During a first stage of heating, the H1 output turns off and remain off between heat calls. If a second stage of heating is called for, the H2 or AUX output energizes the Emergency/Aux heating. If a thermostat calls for W2 only, only the H2 output energizes. The Heating Fan On Delay and Heating Fan Off Delay are used.

## SSE&CCSVAV
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point | Settting value
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level | 4 (Must be set for CCS Operation)
|  | OccMode | Commission>HVACZone>OccMode | 29518 | Schedule (Must be set for CCS Operation)
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | Not Set (Do Not Set at SSE Board for CCS)
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | No (Must be set for CCS Operation)
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level | Wired Field Bus = BACnet MSTP (Must be set for CCS Operation)
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | OFF
|  | Alarms | Alarms |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level | default 1(Do not change for CCS)
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level | Auto or 1200-76800(Set to Auto for CCS)
|  | Unit Name | Details>Unit>Name | Set at board level
|  | Rooftop Controller | Details>Service>Factory>Misc>RooftopControllerType> | Set at board level | Variable (Must be set for CCS Operation)
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>RTU | Set at board level | RTU (Must be set ofr CCS Operation)
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level | Current Version 3.0.0.1072
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level | "TRUE" or "FALSE"
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | Occupied/ Unoccupied
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | ON/OFF
|  | Self Test | Self Test>Start | Set at board Level | Start, Pause, Cancel, Status, Reset
|  | Cooling Adaptive Tuning Enabled | Details>Control>Clg>Setup>ClgAdapTunEn | 29882 | "Yes" or "No"
|  | Heating Adaptive Tuning Enabled | Details>Control>Htg>Setup>HtgAdapTunEn | 29881 | "Yes" or "No"
|  | Time | Update>Time | Set at Board Level | 24 hours Military Format
FAN SETUP/STATUS
|  | Fan Control | Summary>Fan>FanCtl-Type | 29555 | Variable
|  | APS Setup | Details>Service>Factory>Standard>APS Setup | 29556 | None or Variable
|  | APS Status | Details>Control>IndoorFan>Status>APS | 29557 | "ON" = APS closed
|  | Duct pressure Set Point | Details>Setpoints>DctPrs-Sp | 29565 | 0-5"wc
|  | Duct pressure Shut down | Details>Control>IndoorFan>Setup>DctShutdownSp | 29568 | 0-5"wc
|  | Net Override Fan Request | Details>Service>Inputs>NetworkInputs>NetFanReq | 29536 | Writable Point to Force blower "ON"
|  | Fan Overload | Details>Control>IndoorFan>Setup>FanOvrload | 29553
|  | Fan Status | Status>Fan-S | 29550
|  | Fan VFD Status | Summary> Fan> FanVFD | 29551
|  | Fan VFD Fault | Details>Control>IndoorFan>Status>FanVFDFlt | 29552
|  | Fan "OFF" Start Heat | Details>Control>IndoorFan>Setup>FanOffStartHeat | 29569 | "NO"
COOLING SETUP/STATUS
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | ON
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | 1 to 4
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | 1 to 4 Circuits (Must equal number of Cooling Stages)
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | 0 to 100 degrees
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | 40 to 65 degrees
|  | Operating VAV Cooling Setpoint | Details>Setpoints>OprVAVClg-Sp | 29607
|  | VAV Clg SA Upper Stpt | Details>Setpoints>SATUp-Sp | 29604 | 60 degree
|  | VAV Clg SA Lower Stpt | Details>Setpoints>SATLo-Sp | 29605 | 55 degree
|  | VAV SA Reset Stpt | Details>Setpoits>SATRst-Sp | 29606 | 72 degree
|  | Cooling Status | Status>Clg-S | 29577 | Displays Cooling Status
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | "YES" or "NO"
|  | Hot Gas Bypass Installed (Present) | Details>Service>Factory>Standard>HGP-Inst | 29623 | "YES" or "NO"
HEATING SETUP/STATUS
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | "ON" if heat is used
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | 1 to 3
|  | Heating OAT Cutout Setpoint | Details>Control>Htg>Setup>HtgOATCutout-Sp | 29711 | 0 to 100 degrees
|  | Morning Warm Up Enabled | Details>Control>Htg>Setup>MornW-En | 29822 | "ON" if MornW used
|  | Morning Warm Up Stpt | Details>Control>Htg>Setup>MornWRAT-Sp | 29823 | 50 to 85 degrees
|  | VAV Occupied Heat | Details>Setpoints>HtgOcc-En | 29722 | "YES" or "NO"
|  | VAV Occupied Heat Stpt | Details>Setpoints>VAVHtgOcc-Sp | 29723 | 40 to 85 degrees
|  | VAV Operating Heat Stpt | Details>Setpoints>VAVOprHtg-Sp | 29726 | Displays set point
|  | VAV Unccupied Heat Stpt | Details>Setpoint>VAVHtgUnocc-Sp | 29725 | 45 to 98 degress
|  | VAV Unccupied Heat Enable | Details>Setpoint>HtgUnocc-En | 29724 | "Yes" or "No"
|  | Supply Air Heating Limit Enabled | Detals>Control>Htg>Setup>SATHtgLimit-En | 29709 | "YES" or "NO"
|  | Supply Air Heating Limit Set point | Details>Control>Htg>Setup>SATHtgLimt-Sp | 29710 | 100 degree to 180 degree
ECONOMIZER SETUP/STATUS
|  | Economizer Enabled | Commission>Econ>Econ-En | 29747 | "YES" or "NO"
|  | Economizer Firware | Controller>SysCntrls>Econ>EconMainVer |  | View at board level or Map Gateway
|  | Economizer Damper Position | Details>Service>Inputs>Sensors>EconDampPos | 29748 | % open
|  | Economizer Minimum Position | Details>Control>Econ>Setup>Econ-MinPos | 29759 | % Open Set point
|  | Economizer OAT Set point | Details>Control>Econ>Setup>EconOAT-SpEn | 29753 | 40 to 80 degrees
|  | Economizer Free Cooling Available | Summary>Econ>Econ-Free | 29749 | "YES" or "NO"
|  | Economizer Mechanical Setup | Details>Control>Econ>Setup>EconMechStp | 29912 | Option B
|  | All Compressor OFF-Economizer | Details>Control>Clg>Setup>AllCompOff-Econ | 29584 | "YES" or "NO"
|  | Econ OA Enthalpy Setpoint | Details>Control>Econ>Setup>EconOAEth-Sp | 29754 | 10 to 50 BTU/Lb
|  | Free Cooling Selection | Details>Control>Econ>Setup>FreeClg-Sel | 29752 | Auto, Dry Bulb, Single or Dual Enthalpy
Power Exhaust Setup/STATUS
|  | Power Exhaust Fan Type | Details>Service>Factory>Econ>ExFType | 29774 | None, Non-Modualting, Modulating, VFD
|  | Power Exhaust Fan Command | Details>Control>PowerEx>Status> | 29775
|  | Power Exhaust Fan Status | Details>Control>PowerEx>Status>ExFan | 29777
|  | Power Exhaust Modulating Damper Output | Summary>PowerEx>EAD-O | 29782
|  | Building Pressure Set Point | Summary>PowerEx>Bldg-Sp | 29780
|  | Econ Damper Position Power Exhaust "OFF" | Summary>PowerEx>EconDmpPosFanOff | 29786
|  | Econ Damper Position Power Exhaust "ON" | Summary>PowerEx>EconDmpPosFanOn | 29785
|  | Power Exhaust Damper Position "OFF" | Commission>PoweEx>ExDmpPosFanOff | 29784
|  | Power Exhaust Damper Position "On" | Commission>PoweEx>ExDmpPosFanOn | 29783
|  | Power Exhaust VFD Output Status | Summary>PowerEx>ExFanVFD | 29776
CO2 Demand Ventilation Setup/STATUS
|  | (CO2) Demand Ventilation Mode | Commission>Dvent>Dvent-Mode | 29765 | Disabled, Controlled by IAQ, Diff Between IAQ & OAQ
|  | (CO2) Demand Ventilation Mode IAQ Set Point | Commission>Dvent>DventIAQ-Sp | 29767 | 0 to 5000 ppm
|  | (CO2) Demand Ventilation Max Econ Damper Position | Commission>Dvent>DVentMaxEconPos | 29766 | range 0% to 100% open
|  | (CO2) OAQ Range | Commission>Dvent>OAQRange | 29548 | 0 ppm to 5000 ppm
|  | (CO2) IAQ Range | Commission>Dvent>IAQRange | 29529 | 0 ppm to 5000 ppm
|  | (CO2) Demand Ventilation Differential Set Point | Commission>Dvent>DVentDiff-Sp | 29768 | 0 ppm to 5000 ppm
Sensor Inputs & Readings
|  | Supply Air Temperature | Details>Service>Inputs>Sensors>SAT | 29564
|  | Return Air Temperature | Details>Service>Inputs>Sensors>RAT | 29764
|  | Operational Outdoor Air Temperature | Details>Zone>Outdoor>OprOAT | 29541
|  | Outdoor Air Temp Source | Details>Zone>Outdoor>OATSrc | 29542
|  | Operational Space Temperature | Details>Zone>Indoor>OprST | 29522
|  | Operational Space Sensor Offset | Details>Zone>Indoor>OprSSO | 29537
|  | Space Temperature Source | Details>Zone>Indoor>STsrc | 29523
|  | Space Sensor Offset Range | Details>Zone>Indoor>SSORange |  | 0 to 5 degrees F setpoint
|  | Space sensor Offset Source | Details>zone>Indoor>SSOSrc | 29538
|  | Space Humidity RAH input | Details>Control>Econ>Status>RAH | 29828
|  | Outdoor Air Humidity Input | Details>Service>Inputs>Sensor>OAH | N/A
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OA-Enth | 29545
|  | Return Air Enthalpy | Details>Control>Econ>Status>RA-Enth | 29763
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OAH-Enth | 29545
|  | Operational Outdoor Air Humidity | Details>Control>Econ>Status>OprOAH | 29544
|  | Net Override Space Temperature | Details>Service>Inputs>NetworkInputs>NetST | 29526 | Writable Point to Space Temp
|  | Net Override Outdoor Air Temperature | Details>Service>Inputs>NetworkInputs>NetOAT | 29543 | Writable Point to OAT
|  | Net Override Indoor Air Quality | Details>Service>Inputs>NetworkInputs>NetIAQ | 29530 | Writable Point to IAQ
|  | Net Override Outdoor Air Quality | Details>Service>Inputs>NetworkInputs>NetOAQ | 29549 | Writable Point to OAQ
|  | Net Override Outdoor Air Humidity | Details>Service>Inputs>NetworkInputs>NetOAH | 29546 | Writable Point to OAH
|  | Net Override Space Humidity | Details>Service>Inputs>NetworkInputs>NetSH | 29533 | Writable Point to Space Humidity
|  | Net Override Space Sensor Offset | Details>Service>Inputs>NetworkInputs>NetSSO | 29540 | Writable Point to Space Sensor offset
|  | Building Pressure | Summary>PowerEx>BldgPres | 29781 | (-).25 to .25"wc
|  | Duct Pressure | Summary>Fan>DctPrs | 29565 | 0-5" wc
|  | (CO2) IAQ Input | Details>Service>Inputs>Sensor>IAQ
|  | (CO2) OAQ Input | Details>Service>Inputs>Sensor>OAQ
|  | Operational IAQ | Summary>Dvent>OprIAQ | 29527
|  | IAQ source | Details>Zone>Indoor>IAQsrc | 29528
|  | Operational OAQ | Summary>Dvent>OprOAQ | 29547
|  | OAQ source | Deatails>Zone>Outdoor>OAQsrc | 29548
HOT GAS REHEAT
|  | Hot Gas Reheat Enabled for Operation | Details>Service>Factory>Standard>HGR-En | 29789 | "YES" or "NO"
|  | Hot Gas Reheat Alternate Operation Enabled | Details>Control>HGR>HGRAlt-En | 29793 | "YES" or "NO"
|  | Hot Gas Reheat Gas Reheat Humidity Setpoint | Details>Control>HGR>HGRHum-SP | 29792 | 0% to 100%
|  | Hot Gas Reheat Alternate Operation Writable | Details>Control>HGR>HGRAltWrite | 29794 | "YES" or "NO"
|  | Hot Gas Reheat Enabled for Unoccupied Operation | Details>Control>HGR>HGRUnocc-En | 29904 | "YES" or "NO"
|  | Hot Gas Reheat Unoccupied Humidity Setpoint | Details>Control>HGR>HGRUnoccHum-Sp | 29903 | 0% to 100%
|  | Hot Gas Reheat Status | Details>Control>HGR>HGR-S | 29791
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus. When setting up for CCS VAV System. Address must be set to 4 to communicate on FC bus to Zone Coordinator zone bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool. When used with CCS OccMode is set to Schedule. This allows CCS to occ/unocc the unit.
Note on B5: cedmonja: This point will occupy and unoccupy the unit.
Note on B6: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B7: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B8: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B10: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B16: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B17: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B18: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B19: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B20: Chad Edmondson: By default "YES" the PID tuning parameters are managed by PRAC+(Pattern Recognition Adaptive Control) algorithm base on either Zone Temperature or Discharge Air Temperature process. PRAC+ can be turned off by changing the value of Cooling Adaptive Tuning Enable to "NO". Doing this will setup the PID to use the process defaults for either Zone Temperature or Discharge Temperature which can be found in the Cooling Adaptive Tuning chart attached to the right.
Note on B25: cedmonja: Variable speed- Sets the SSE board to operate as a VAV unit and control fan speed according to static pressure. Fixed Variable-Sets the SSE board to operate according to a 7 fan speed selection when the blower is VFD controlled. Single Speed-Sets the SSE Board to operate according to 100% fan operation. With no VFD applied to RTU.
Note on B26: cedmonja: None-Sets board not to recognize APS if not being used. Variable-allows operation of APS applied to a SSE VAV setup.
Note on B30: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B35: cedmonja: Yes-Prevents blower operation request from the start of 1 stage heat commmand until a 24VAC input is recognized at the MV pin and the FanOnDlyHeat expires. No-Ignores this operation. Note: When board is set to variable operation. This point is only visable when fan control type is set to Fixed Variable or Single Speed. You must set the point to "No" in Variable operation if you do not want the fan to shutdown according to timers.
Note on B38: cedmonja: VAV Cooling Operation: If the operational space temperature rises + 2°F or more above the VAV Cooling Supply Air Temperature Reset Setpoint, the VAV Cooling Supply Air Temp Lower Setpoint is used for the Operational VAV Cooling Setpoint. If the operational space temperature falls below the Supply Air Temperature Reset Setpoint the Supply Air Temperature Upper Setpoint is used for the Operational VAV Cooling Setpoint.
Note on B41: Chad Edmondson: #1 of circuits are set to 1 when used with a series 40 condensing unit. This will allow proper operation of high and low pressure switches.
Note on B42: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B43: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B44: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B46: cedmonja: The VAV cooling SAT setpoint in use; with OprST above SATRst-Sp is SATLo-Sp, with OprST below SATRst-Sp is SATUp-Sp; cooling operation requests are initiated when OprST rises above this setpoint.
Note on B51: cedmonja: At the initiation of each cooling demand the compressor with the lowest run hours energizes first. The compressor with the next number of lowest run hours energizes next, and so on. At the termination of the cooling demand, the compressor with the most run hours stage off in reverse order.
Note on B52: cedmonja: If lead lag is enabled. Hot Gas Bypass will operate in this sequence if set to "YES". VAV operation: If compressor operation is ongoing and C1 is not running, and fan speed drops below 50%, compressors stage off and stage back on in order. If fan speed is greater than 50% and the SAT is less than 45°F, the Lead/Lag function disables. CV operation: If the SAT is less than 45°F, the Lead/Lag function disables.
Note on B59: cedmonja: Setpoint does not allow heating operation when Operational OAT goes above the setpoint.
Note on B60: cedmonja: With a BI occupied command the supply fan turns on for a five minute stabilization period and then operating space temperature is compared to morning warm-up return air temp setpoint. If the value is equal to or below the morning warm-up return air temp setpoint, all heat stages operate for at least 5 minutes. If the value is above the morning warmup return air temp setpoint, the control goes into Occupied mode.
Note on B66: cedmonja: VAV Unoccupied Heat Operation: YES- Allow VAV heating in unoccupied operation. NO-Does not allow VAV heating in unoccupied operation. Control must be in an unoccupied mode and not in morning warm-up mode. If the operational space temperature drops lower than the VAV Heating Unoccupied Setpoint all heat stages energize with approximately 30 seconds delay between stages. Heat remains energized until the operational space temperature reaches the VAV Heating Unoccupied Setpoint + 3°F. Any time the control enters the heat mode, VAV box contact closes. Warning: If the unit is in a heating mode, the control continues to vary the DC output to control duct pressure to the Duct Static Pressure setpoint. Therefore, in any VAV heating mode, all VAV boxes must be commanded open far enough to get adequate airflow to support the heating function and to prevent the heat section high temperature limit switches from opening.
Note on B71: cedmonja: Yes-enables economizer function. No-disables economizer function.
Note on B73: cedmonja: Value displays % economizer damper is open.
Note on B74: cedmonja: Economizer damper minimum % open setpoint during occupied mode.
Note on B75: cedmonja: Dry bulb economizer setpoint. When OAT drops below set point economizer functions starts.
Note on B76: cedmonja: Yes-Economizer free cooling is available. No-Economizer free cooling is not available.
Note on B77: cedmonja: Option A-(Do Not Use) Economizer damper position and/or time triggers compressor operation to supplement free cooling. Option B- Supply air temperature with VAV supply air temperature(upper/lower) setpoint triggers compressor operation to supplement free cooling.
Note on B78: cedmonja: Yes-Does not allow compressor operation during free cooling. No-allows compressor operation durig free cooling.
Note on B79: cedmonja: Single enthalpy free cooling setpoint. When Outside Air Enthalpy is below setpoint free cooling is available.
Note on B83: cedmonja: With the series 10 & 20 RTU the only curren option is Non-Modulating Power Exhaust.
Note on B95: cedmonja: Demand Ventilation mode selection. Disabled-No Demand Ventilation Function. Controlled by IAQ- Enables Demand Ventilation control with IAQ input. Differential between IAQ & OAQ- Enables Demand Ventilation control with a comparison between IAQ & OAQ.
Note on B99: cedmonja: IAQ sensor range.
Note on B131: cedmonja: the source of the indoor air quality input in use; Local is from the economizer board IAQ 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates IAQ input is currently not present
Note on B132: cedmonja: The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present.
Note on B133: cedmonja: the source of the outdoor air quality input in use; Local is from economizer board OAQ 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
Note on B136: cedmonja: Normal Occupied Operation Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 output energizes and the AUX-HGR output energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 output energizes but the AUX-HGR output de-energizes. Any additional cooling demands energize compressor outputs, but do not change the status of the AUX-HGR output. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas
Note on B137: cedmonja: Alternate Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for both first and second cooling stages and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and C2 outputs energize and AUX-HGR de-energizes. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas Reheat Humidity Setpoint.
Note on B139: cedmonja: YES- Allows access to hot gas reheat moode selection in HGRAlt-En. NO-Does not allow access to hot gas reheat mode selection in HGRAlt-En.
Note on B140: cedmonja: YES- Allows hot gas reheat operation when occupancy status is Unoccupied. NO- Does not allow hot has reheat operation when occupancy status is Unoccupied.

## SSE&CCS-COBP
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point | Settting value
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level | 4 (Must be set for CCS Operation)
|  | OccMode | Commission>HVACZone>OccMode | 29518 | Schedule (Must be set for CCS Operation)
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | Not Set (Do Not Set at SSE Board for CCS)
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | No (Must be set for CCS Operation)
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level | Wired Field Bus=BACnet MSTP (Must be set for CCS Operation)
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | OFF
|  | Alarms | Alarms |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level | default 1(Do not change for CCS)
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level | Auto or 1200-76800(Set to Auto for CCS)
|  | Unit Name | Details>Unit>Name | Set at board level
|  | Rooftop Controller | Details>Service>Factory>Misc>RooftopControllerType> | Set at board level | Changeover Bypass (Must be set for CCS Operation)
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>RTU | Set at board level | RTU(Must be set for CCS Operation)
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level | Current Version 3.0.0.1072
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level | "TRUE" or "FALSE"
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | Occupied/ Unoccupied
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | ON/OFF
|  | Self Test | Self Test>Start | Set at board Level | Start, Pause, Cancel, Status, Reset
|  | Cooling Adaptive Tuning Enabled | Details>Control>Clg>Setup>ClgAdapTunEn | 29882 | "Yes" or "No"
|  | Heating Adaptive Tuning Enabled | Details>Control>Htg>Setup>HtgAdapTunEn | 29881 | "Yes" or "No"
|  | Time | Update>Time | Set at Board Level | 24 hours Military Format
FAN SETUP/STATUS
|  | Fan Control | Summary>Fan>FanCtl-Type | 29555 | Fixed Variable(7speed fan selection) or Single Speed
|  | APS Setup | Details>Service>Factory>Standard>APS Setup | 29556 | None or Constant
|  | APS Status | Details>Control>IndoorFan>Status>APS | 29557 | ON = APS closed
|  | Net Override Fan Request | Details>Service>Inputs>NetworkInputs>NetFanReq | 29536 | Writable Point to Force blower "ON"
|  | Fan Only Command VFD speed % | Commission> IndoorFan>FanOnly-%Cmd | 29570 | set to 0% to 100% speed reference
|  | 1 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>1ClgStg-%Cmd | 29571 | set to 0% to 100% speed reference
|  | 1 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>1HtgStg-%Cmd | 29573 | set to 0% to 100% speed reference
|  | 2 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>2ClgStg-%Cmd | 29572 | set to 0% to 100% speed reference
|  | 3 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>3ClgStg-%Cmd | 29819 | set to 0% to 100% speed reference
|  | 3 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>3HtgStg-%Cmd | 29821 | set to 0% to 100% speed reference
|  | 4 Stage Coolig Command VFD speed % | Details>Control>IndoorFan>Setup>4StageStg-%Cmd | 29820 | set to 0% to 100% speed reference
|  | Fan "OFF" Delay Cool | Details>Control>IndoorFan>Setup.FanOffDlyCool | 29559 | 0 to 255 second timer
|  | Fan "OFF" Delay Heat | Details>Control>IndoorFan>Setup>FanOffDlyHeat | 29561 | 0 to 255 second timer
|  | Fan "OFF" Start Heat | Details>Control>IndoorFan>Setup>FanoffStartHeat | 29569 | "YES" or "NO"
|  | Fan "ON" Delay Cool | Details>Control>IndoorFan>Setup>FanOnDlyCool | 29558 | 0 to 30 second timer
|  | Fan "ON" Delay Heat | Details>Control>IndoorFan>Setup>FanOnDlyHeat | 29560 | 0 to 30 second timer
|  | Fan "ON" Occupied | Details>Control>IndoorFan>Setup>FanOnOcc | 29568 | "YES" or "NO"
|  | Fan Overload | Details>Control>IndoorFan>Setup>FanOvrload | 29553
|  | Fan Status | Status>Fan-S | 29550
|  | Fan VFD Status | Summary> Fan> FanVFD | 29551
|  | Fan VFD Fault | Details>Control>IndoorFan>Status>FanVFDFlt | 29552
COOLING SETUP/STATUS
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | "YES" or "NO"
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | 1 to 4
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | 1 to 4 Circuits (Must equal number of Cooling Stages)
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | "YES" or "NO"
|  | Hot Gas Bypass Installed (Present) | Details>Service>Factory>Standard>HGP-Inst | 29623 | "YES" or "NO"
|  | Cooling Status | Status>Clg-S | 29577 | Displays Cooling Status
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | 0 to 100 degrees
|  | Low Ambient Enabled | Details>Control>Clg>Setup>LowAmb-En | 29928 | "YES" or "NO"
|  | Low Ambient Operation Setpoint | Detials>Control>Clg>Setup>LowAmb10On5OffSp | 29585 | 0 to 60 degrees
|  | Constant Volume Occupied Cooling Setpoint | Details>Setpoints>ClgOcc-Sp | 29608 | range 45 to 98 degrees
|  | Constant Volume Unoccupied Cooling Setpoint | Details>Setpoints>ClgUnocc-Sp | 29609 | range 46 to 99 degress
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | 40 to 65 degrees
|  | Compressor 1 Command | Details>Control>Clg>Stage 1>C1-Cl | 29611
|  | Compressor 1 Status | Details>Control>Clg>Stage1>C1-S | 29615
|  | Compressor 1 Enabled | Details>Control>Clg>Stage1>C1-En | 29619
|  | Compressor 1 Accumulated Run Time | Details>Control>Clg>Stage1>C1RunTim | 29627
|  | Compressor 2 Command | Details>Control>Clg>Stage2>C2-Cl | 29612
|  | Compressor 2 Status | Details>Control>Clg>Stage2>C2-S | 29616
|  | Compressor 2 enabled | Details>Control>Clg>Stage2>C2-En | 29620
|  | Compressor 2 Accumulated Run time | Details>Control>Clg>Stage2>C2RunTim | 29628
|  | Compressor 3 Command | Details>Control>Clg>Stage3>C3-Cl | 29613
|  | Compressor 3 Status | Details>Control>Clg>Stage3>C3-S | 29617
|  | Compressor 3 Enabled | Details>Control>Clg>Stage3>C3-En | 29621
|  | Compressor 3 Accumulated Run Time | Details>Control>Clg>Stage3>C3RunTim | 29629
|  | Compressor 4 Command | Details>Control>Clg>Stage4>C4-Cl | 29614
|  | Compressor 4 Status | Details>Control>Clg>Stage4>C4-S | 29618
|  | Compressor 4 Enabled | Details>Control>Clg>Stage4>C4-En | 29622
|  | Compressor 4 Accumulated Run Time | Details>Control>Clg>Stage4>C4RunTim | 29630
HEATING SETUP/STATUS
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | "YES" or "NO"
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | 1 to 3
|  | Heating OAT Cutout Setpoint | Details>Control>Htg>Setup>HtgOATCutout-Sp | 29711 | 0 to 100 degrees
|  | Constant Volume Occupied Heating Setpoint | Details>Setpoints>CVHtgOcc-Sp | 29728 | Range 46 to 99 degrees
|  | Constant Volume Unoccuped Heating Setpoint | Details>Setpoints>CVHtgUnocc-Sp | 29729 | Range 45 to 98 degrees
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29739
|  | Heating Stage 1 Command | Details>Control>Htg>Stage1>H1 | 29732
|  | Heating Stage 1 Status | Details>Cotrol>Htg>Stage1>H1-S | 29735
|  | Heating Stage 2 Command | Details>Control>Htg>Stage2>H2 | 29733
|  | Heating Stage 2 Status | Details>Cotrol>Htg>Stage2>H2-S | 29736
|  | Heating Stage 3 Command | Details>Control>Htg>Stage3>H3 | 29734
|  | Heating Stage 3 Status | Details>Cotrol>Htg>Stage3>H3-S | 29737
|  | Supply Air Heating Limit Enabled | Detals>Control>Htg>Setup>SATHtgLimit-En | 29709 | "YES" or "NO"
|  | Supply Air Heating Limit Set point | Details>Control>Htg>Setup>SATHtgLimt-Sp | 29710 | 100 degree to 180 degree
ECONOMIZER SETUP/STATUS
|  | Economizer Enabled | Commission>Econ>Econ-En | 29747 | "YES" or "NO"
|  | Economizer Firware | Controller>SysCntrls>Econ>EconMainVer |  | View at board level or Map Gateway
|  | Economizer Damper Position | Details>Service>Inputs>Sensors>EconDampPos | 29748 | % open
|  | Economizer Minimum Position | Details>Control>Econ>Setup>Econ-MinPos | 29759 | % Open Set point
|  | Economizer OAT Set point | Details>Control>Econ>Setup>EconOAT-SpEn | 29753 | 40 to 80 degrees
|  | Economizer Free Cooling Available | Summary>Econ>Econ-Free | 29749 | "YES" or "NO"
|  | Economizer Mechanical Setup | Details>Control>Econ>Setup>EconMechStp | 29912 | Option B
|  | All Compressor OFF-Economizer | Details>Control>Clg>Setup>AllCompOff-Econ | 29584 | "YES" or "NO"
|  | Econ OA Enthalpy Setpoint | Details>Control>Econ>Setup>EconOAEth-Sp | 29754 | 10 to 50 BTU/Lb
|  | Free Cooling Selection | Details>Control>Econ>Setup>FreeClg-Sel | 29752 | Auto, Dry Bulb, Single or Dual Enthalpy
|  | Low Ambient Minimum Position | Details>Control>Econ>Setup>LowAmb-MinPos | 29756 | 0% to 100% econ damper open
|  | Low Ambient Set point | Details>Control>Econ>Setup>LowAmb-Sp | 29755 | 0 to 60 degrees
|  | Low Speed Fan Minimum Position | Details>Control>Econ>LowSpeedFan-MinPos | 29808 | 0% to 100% econ damper open
Power Exhaust Setup/STATUS
|  | Power Exhaust Fan Type | Details>Service>Factory>Econ>ExFType | 29774 | None, Non-Modualting, Modulating, VFD
|  | Power Exhaust Fan Command | Details>Control>PowerEx>Status> | 29775
|  | Power Exhaust Fan Status | Details>Control>PowerEx>Status>ExFan | 29777
|  | Power Exhaust Modulating Damper Output | Summary>PowerEx>EAD-O | 29782
|  | Building Pressure Set Point | Summary>PowerEx>Bldg-Sp | 29780
|  | Econ Damper Position Power Exhaust "OFF" | Summary>PowerEx>EconDmpPosFanOff | 29786
|  | Econ Damper Position Power Exhaust "ON" | Summary>PowerEx>EconDmpPosFanOn | 29785
|  | Power Exhaust Damper Position "OFF" | Commission>PoweEx>ExDmpPosFanOff | 29784
|  | Power Exhaust Damper Position "On" | Commission>PoweEx>ExDmpPosFanOn | 29783
|  | Power Exhaust VFD Output Status | Summary>PowerEx>ExFanVFD | 29776
CO2 Demand Ventilation Setup/STATUS
DO NOT!!! set at board level for CCS |  | (CO2) Demand Ventilation Mode | Commission>Dvent>Dvent-Mode | 29765 | Disabled, Controlled by IAQ, Diff Between IAQ & OAQ
COBP System. This is set at Zone level |  | (CO2) Demand Ventilation Mode IAQ Set Point | Commission>Dvent>DventIAQ-Sp | 29767 | 0 to 5000 ppm
for each zone. A CO2 sensor must be |  | (CO2) Demand Ventilation Max Econ Damper Position | Commission>Dvent>DVentMaxEconPos | 29766 | range 0% to 100% open
installed & setup for each zone requiring |  | (CO2) OAQ Range | Commission>Dvent>OAQRange | 29548 | 0 ppm to 5000 ppm
CO2 control. |  | (CO2) IAQ Range | Commission>Dvent>IAQRange | 29529 | 0 ppm to 5000 ppm
|  | (CO2) Demand Ventilation Differential Set Point | Commission>Dvent>DVentDiff-Sp | 29768 | 0 ppm to 5000 ppm
Sensor Inputs & Readings
|  | Supply Air Temperature | Details>Service>Inputs>Sensors>SAT | 29564
|  | Return Air Temperature | Details>Service>Inputs>Sensors>RAT | 29764
|  | Operational Outdoor Air Temperature | Details>Zone>Outdoor>OprOAT | 29541
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29730
|  | Constant Volume Operating Cooling Setpoint | Details>Setpoints>OprCVClg-Sp | 29610
|  | Operational Space Temperature | Details>Zone>Indoor>OprST | 29522
|  | Space Temperature Source | Details>Zone>Indoor>STsrc | 29523
|  | Space Humidity RAH input | Details>Control>Econ>Status>RAH | 29828
|  | Outdoor Air Humidity Input | Details>Service>Inputs>Sensor>OAH | N/A
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OA-Enth | 29545
|  | Return Air Enthalpy | Details>Control>Econ>Status>RA-Enth | 29763
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OAH-Enth | 29545
|  | Operational Outdoor Air Humidity | Details>Control>Econ>Status>OprOAH | 29544
|  | Net Override Space Temperature | Details>Service>Inputs>NetworkInputs>NetST | 29526 | Writable Point to Space Temp
|  | Net Override Outdoor Air Temperature | Details>Service>Inputs>NetworkInputs>NetOAT | 29543 | Writable Point to OAT
|  | Net Override Indoor Air Quality | Details>Service>Inputs>NetworkInputs>NetIAQ | 29530 | Writable Point to IAQ
|  | Net Override Outdoor Air Quality | Details>Service>Inputs>NetworkInputs>NetOAQ | 29549 | Writable Point to OAQ
|  | Net Override Outdoor Air Humidity | Details>Service>Inputs>NetworkInputs>NetOAH | 29546 | Writable Point to OAH
|  | Net Override Space Humidity | Details>Service>Inputs>NetworkInputs>NetSH | 29533 | Writable Point to Space Humidity
|  | Net Override Space Sensor Offset | Details>Service>Inputs>NetworkInputs>NetSSO | 29540 | Writable Point to Space Sensor offset
|  | Building Pressure | Summary>PowerEx>BldgPres | 29781 | (-).25 to .25"wc
|  | (CO2) IAQ Input | Details>Service>Inputs>Sensor>IAQ | N/A
|  | (CO2) OAQ Input | Details>Service>Inputs>Sensor>OAQ | N/A
|  | Operational IAQ | Summary>Dvent>OprIAQ | 29527
|  | IAQ source | Details>Zone>Indoor>IAQsrc | 29528
|  | Operational OAQ | Summary>Dvent>OprOAQ | 29547
|  | OAQ source | Deatails>Zone>Outdoor>OAQsrc | 29548
HOT GAS REHEAT
|  | Hot Gas Reheat Enabled for Operation | Details>Service>Factory>Standard>HGR-En | 29789 | "YES" or "NO"
|  | Hot Gas Reheat Alternate Operation Enabled | Details>Control>HGR>HGRAlt-En | 29793 | "YES" or "NO"
|  | Hot Gas Reheat Gas Reheat Humidity Setpoint | Details>Control>HGR>HGRHum-SP | 29792 | 0% to 100%
|  | Hot Gas Reheat Alternate Operation Writable | Details>Control>HGR>HGRAltWrite | 29794 | "YES" or "NO"
|  | Hot Gas Reheat Enabled for Unoccupied Operation | Details>Control>HGR>HGRUnocc-En | 29904 | "YES" or "NO"
|  | Hot Gas Reheat Unoccupied Humidity Setpoint | Details>Control>HGR>HGRUnoccHum-Sp | 29903 | 0% to 100%
|  | Hot Gas Reheat Status | Details>Control>HGR>HGR-S | 29791
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus. When setting up for CCS COBP System. Address must be set to 4 to communicate on FC bus to Zone Coordinator zone bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool. When used with CCS OccMode is set to Schedule. This allows CCS to occ/unocc the unit.
Note on B5: cedmonja: This point will occupy and unoccupy the unit.
Note on B6: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B7: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B8: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B10: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B16: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B17: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B18: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B19: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B20: Chad Edmondson: By default "YES" the PID tuning parameters are managed by PRAC+(Pattern Recognition Adaptive Control) algorithm base on either Zone Temperature or Discharge Air Temperature process. PRAC+ can be turned off by changing the value of Cooling Adaptive Tuning Enable to "NO". Doing this will setup the PID to use the process defaults for either Zone Temperature or Discharge Temperature which can be found in the Cooling Adaptive Tuning chart attached to the right.
Note on B25: cedmonja: Variable speed- Sets the SSE board to operate as a VAV unit and control fan speed according to static pressure. Fixed Variable-Sets the SSE board to operate according to a 7 fan speed selection when the blower is VFD controlled. Single Speed-Sets the SSE Board to operate according to 100% fan operation. With no VFD applied to RTU.
Note on B26: cedmonja: None-Sets board not to recognize APS if not being used. Variable-allows operation of APS applied to a SSE VAV setup.
Note on B28: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B38: cedmonja: Yes-Prevents blower operation request from the start of 1 stage heat commmand until a 24VAC input is recognized at the MV pin and the FanOnDlyHeat expires. No-Ignores this operation.
Note on B39: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B41: cedmonja: Yes-Permits continuous fan operation when in occupied mode. No-Only permits fan during a call for heat or cool.
Note on B51: Chad Edmondson: #1 of circuits are set to 1 when used with a series 40 condensing unit. This will allow proper operation of high and low pressure switches.
Note on B52: cedmonja: At the initiation of each cooling demand the compressor with the lowest run hours energizes first. The compressor with the next number of lowest run hours energizes next, and so on. At the termination of the cooling demand, the compressor with the most run hours stage off in reverse order.
Note on B53: cedmonja: If lead lag is enabled. Hot Gas Bypass will operate in this sequence if set to "YES". VAV operation: If compressor operation is ongoing and C1 is not running, and fan speed drops below 50%, compressors stage off and stage back on in order. If fan speed is greater than 50% and the SAT is less than 45°F, the Lead/Lag function disables. CV operation: If the SAT is less than 45°F, the Lead/Lag function disables.
Note on B55: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B56: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B57: cedmonja: If Cooling OAT Cutout Enble is Yes, the compressor is not permitted if the OAT is less than the cooling OAT Cutout. If Cooling OAT Cutout Enable is NO. the compressor cycles 10 minutes On and 5 minutes Off if the OAT is less than the LowAmb10On5Off Setpoint. If a compressor is in the 10 min On cycle and the evaportator temperature (EC1 thru EC4) drops below 26 degrees F. the compressor output de-endergizes and the 5 minute ASCD starts. After 5 minutes ASCD expires, the compressor ouput is permitted. Anytime the compressor output de-energizes due to the evaporator coil temperature protection it does not count towards a hard compressor lockout.
Note on B61: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B84: cedmonja: Setpoint does not allow heating operation when Operational OAT goes above the setpoint.
Note on B98: cedmonja: Yes-enables economizer function. No-disables economizer function.
Note on B100: cedmonja: Value displays % economizer damper is open.
Note on B101: cedmonja: Economizer damper minimum % open setpoint during occupied mode.
Note on B102: cedmonja: Dry bulb economizer setpoint. When OAT drops below set point economizer functions starts.
Note on B103: cedmonja: Yes-Economizer free cooling is available. No-Economizer free cooling is not available.
Note on B104: cedmonja: Option A-(Do Not Use) Economizer damper position and/or time triggers compressor operation to supplement free cooling. Option B- Supply air temperature with VAV supply air temperature(upper/lower) setpoint triggers compressor operation to supplement free cooling.
Note on B105: cedmonja: Yes-Does not allow compressor operation during free cooling. No-allows compressor operation durig free cooling.
Note on B106: cedmonja: Single enthalpy free cooling setpoint. When Outside Air Enthalpy is below setpoint free cooling is available.
Note on B115: cedmonja: With the series 10 & 20 RTU the only curren option is Non-Modulating Power Exhaust.
Note on B127: cedmonja: Demand Ventilation mode selection. Disabled-No Demand Ventilation Function. Controlled by IAQ- Enables Demand Ventilation control with IAQ input. Differential between IAQ & OAQ- Enables Demand Ventilation control with a comparison between IAQ & OAQ.
Note on B131: cedmonja: IAQ sensor range.
Note on B138: cedmonja: This point will reflect the offset + or - range of the occupied heating setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B139: cedmonja: This point will reflect the offset + or - range of the occupied cooling setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B160: cedmonja: the source of the indoor air quality input in use; Local is from the economizer board IAQ 0-10 VDC input, Network Sensor is from SA BUS NetSensor, BAS Override is from FC BUS communicated value, Unreliable indicates IAQ input is currently not present
Note on B161: cedmonja: The buffered outdoor air humidity in use; may be from economizer board OAH 0-10 VDC input or FC BUS communicated value sources; Input Unreliable indicates OAH input is currently not present.
Note on B162: cedmonja: the source of the outdoor air quality input in use; Local is from economizer board OAQ 0-10 VDC input, BAS Override is from FC BUS communicated value, Unreliable indicates OAH input is currently not present
Note on B165: cedmonja: Normal Occupied Operation Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 output energizes and the AUX-HGR output energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 output energizes but the AUX-HGR output de-energizes. Any additional cooling demands energize compressor outputs, but do not change the status of the AUX-HGR output. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas
Note on B166: cedmonja: Alternate Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for both first and second cooling stages and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and C2 outputs energize and AUX-HGR de-energizes. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas Reheat Humidity Setpoint.
Note on B168: cedmonja: YES- Allows access to hot gas reheat moode selection in HGRAlt-En. NO-Does not allow access to hot gas reheat mode selection in HGRAlt-En.
Note on B169: cedmonja: YES- Allows hot gas reheat operation when occupancy status is Unoccupied. NO- Does not allow hot has reheat operation when occupancy status is Unoccupied.

## SSE&CCS-SingleZone
| Operation | SSE Point | SSE & Map Gateway Path | BACnet Point | Settting value
SYSTEM SETUP
|  | Address | Commission>Network>Address | Set at board level | 18 to 41(Must be set for CCS Operation)
|  | OccMode | Commission>HVACZone>OccMode | 29518 | Schedule (Must be set for CCs Operation)
|  | NetOcc | Details>Service>Inputs>NetworkInputs>NetOcc | 29520 | Not Set (Do Not Set at SSE Board for CCS)
|  | TstatOnly | Details>Service>Inputs>Thermostat>Tstat-Only | 29514 | No (Must be set for CCS Operation)
|  | Wired Field Bus | Controller>Network>FCBusMode>Wired Field Bus | Set at board level | Wired Field Bus=BACnet MSTP(Must be set for CCS Operation)
|  | SZVAVEn | Details>Service>Factory>Misc>SZVAVEn | 29908 | OFF
|  | Alarms | Alarms |  | See alarm tab
|  | Device ID | Controller>Network>DeviceID | Set at board level | default 1(Do not change for CCS)
|  | Baud Rate | Controller>Network>OprBaudRate | Set at board level | Auto or 1200-76800(Set to Auto for CCS)
|  | Unit Name | Details>Unit>Name | Set at board level
|  | Rooftop Controller | Details>Service>Factory>Misc>RooftopControllerType> | Set at board level | Constant Volume (Must be set for CCS Operation)
|  | Equipment Type | Details>Service>Factory>Misc>RooftopEquipment>RTU | Set at board level | RTU (Must be set for CCS Operation)
|  | SSE Board Firmware Version | Update>ViewVersion | View at Board level | Current Version 3.0.0.1072
|  | Relearn | Controller>SysCntlrs>Misc>Relearn | Set at board level | "TRUE" or "FALSE"
|  | Operational Occupancy | Details>Zone>Indoor>OprOcc | 29517 | Occupied/ Unoccupied
|  | Reset Lockout | Details>Unit>ResetLO | 29826 | ON/OFF
|  | Self Test | Self Test>Start | Set at board Level | Start, Pause, Cancel, Status, Reset
|  | Cooling Adaptive Tuning Enabled | Details>Control>Clg>Setup>ClgAdapTunEn | 29882 | "Yes" or "No"
|  | Heating Adaptive Tuning Enabled | Details>Control>Htg>Setup>HtgAdapTunEn | 29881 | "Yes" or "No"
|  | Time | Update>Time | Set at Board Level | 24 hours Military Format
FAN SETUP/STATUS
|  | Fan Control | Summary>Fan>FanCtl-Type | 29555 | Fixed Variable(8speed fan selection) or Single Speed
|  | APS Setup | Details>Service>Factory>Standard>APS Setup | 29556 | None or Constant
|  | APS Status | Details>Control>IndoorFan>Status>APS | 29557 | ON = APS closed
|  | Net Override Fan Request | Details>Service>Inputs>NetworkInputs>NetFanReq | 29536 | Writable Point to Force blower "ON"
|  | Fan Only Command VFD speed % | Commission> IndoorFan>FanOnly-%Cmd | 29570 | set to 0% to 100% speed reference
|  | 1 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>1ClgStg-%Cmd | 29571 | set to 0% to 100% speed reference
|  | 1 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>1HtgStg-%Cmd | 29573 | set to 0% to 100% speed reference
|  | 2 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>2ClgStg-%Cmd | 29572 | set to 0% to 100% speed reference
|  | 3 Stage Cooling Command VFD speed % | Details>Control>IndoorFan>Setup>3ClgStg-%Cmd | 29819 | set to 0% to 100% speed reference
|  | 3 Stage Heating Command VFD speed % | Details>Control>IndoorFan>Setup>3HtgStg-%Cmd | 29821 | set to 0% to 100% speed reference
|  | 4 Stage Coolig Command VFD speed % | Details>Control>IndoorFan>Setup>4StageStg-%Cmd | 29820 | set to 0% to 100% speed reference
|  | Fan "OFF" Delay Cool | Details>Control>IndoorFan>Setup.FanOffDlyCool | 29559 | 0 to 255 second timer
|  | Fan "OFF" Delay Heat | Details>Control>IndoorFan>Setup>FanOffDlyHeat | 29561 | 0 to 255 second timer
|  | Fan "OFF" Start Heat | Details>Control>IndoorFan>Setup>FanoffStartHeat | 29569 | "YES" or "NO"
|  | Fan "ON" Delay Cool | Details>Control>IndoorFan>Setup>FanOnDlyCool | 29558 | 0 to 30 second timer
|  | Fan "ON" Delay Heat | Details>Control>IndoorFan>Setup>FanOnDlyHeat | 29560 | 0 to 30 second timer
|  | Fan "ON" Occupied | Details>Control>IndoorFan>Setup>FanOnOcc | 29568 | "YES" or "NO"
|  | Fan Overload | Details>Control>IndoorFan>Setup>FanOvrload | 29553
|  | Fan Status | Status>Fan-S | 29550
|  | Fan VFD Status | Summary> Fan> FanVFD | 29551
|  | Fan VFD Fault | Details>Control>IndoorFan>Status>FanVFDFlt | 29552
COOLING SETUP/STATUS
|  | Cooling Enabled | Commission>Clg>Clg-En | 29575 | "YES" or "NO"
|  | Staged Cooling Command | Details>Control>Clg>Status>StgClgCmd | 29922 | 0% to 100%
|  | # Cooling Stages | Details>Service>Factory>Standard>#ClgStgs | 29576 | 1 to 4
|  | Number of Refrigeration Systems | Details>Service>Factory>standard>#refrigsys | 29890 | 1 to 4 Circuits (Must equal number of Cooling Stages)
|  | Lead Lag Enabled | Details>Control>Clg>Setup>LeadLag-En | 29579 | "YES" or "NO"
|  | Hot Gas Bypass Installed (Present) | Details>Service>Factory>Standard>HGP-Inst | 29623 | "YES" or "NO"
|  | Cooling Status | Status>Clg-S | 29577 | Displays Cooling Status
|  | OAT Cooling Lockout Enable | Details>Control>Clg>Setup>ClgOATCutout-En | 29581 | "YES" or "NO"
|  | OAT Cooling Lockout Setpoint | Details>Control>Clg>Setup>ClgOATCutout | 29582 | 0 to 100 degrees
|  | Low Ambient Enabled | Details>Control>Clg>Setup>LowAmb-En | 29928 | "YES" or "NO"
|  | Low Ambient Operation Setpoint | Detials>Control>Clg>Setup>LowAmb10On5OffSp | 29585 | 0 to 60 degrees
|  | Constant Volume Occupied Cooling Setpoint | Details>Setpoints>ClgOcc-Sp | 29608 | range 45 to 98 degrees
|  | Constant Volume Unoccupied Cooling Setpoint | Details>Setpoints>ClgUnocc-Sp | 29609 | range 46 to 99 degress
|  | Supply Air Cool Limit Enable | Details>Control>Clg>Setup>SATCoolLimit-En | 29590 | "YES" or "NO"
|  | Supply Air Cool Limit Set Point | Details>Control>Clg>Setup>-SATCoolLimit-Sp | 29591 | 40 to 65 degrees
|  | Compressor 1 Command | Details>Control>Clg>Stage 1>C1-Cl | 29611
|  | Compressor 1 Status | Details>Control>Clg>Stage1>C1-S | 29615
|  | Compressor 1 Enabled | Details>Control>Clg>Stage1>C1-En | 29619
|  | Compressor 1 Accumulated Run Time | Details>Control>Clg>Stage1>C1RunTim | 29627
|  | Compressor 2 Command | Details>Control>Clg>Stage2>C2-Cl | 29612
|  | Compressor 2 Status | Details>Control>Clg>Stage2>C2-S | 29616
|  | Compressor 2 enabled | Details>Control>Clg>Stage2>C2-En | 29620
|  | Compressor 2 Accumulated Run time | Details>Control>Clg>Stage2>C2RunTim | 29628
|  | Compressor 3 Command | Details>Control>Clg>Stage3>C3-Cl | 29613
|  | Compressor 3 Status | Details>Control>Clg>Stage3>C3-S | 29617
|  | Compressor 3 Enabled | Details>Control>Clg>Stage3>C3-En | 29621
|  | Compressor 3 Accumulated Run Time | Details>Control>Clg>Stage3>C3RunTim | 29629
|  | Compressor 4 Command | Details>Control>Clg>Stage4>C4-Cl | 29614
|  | Compressor 4 Status | Details>Control>Clg>Stage4>C4-S | 29618
|  | Compressor 4 Enabled | Details>Control>Clg>Stage4>C4-En | 29622
|  | Compressor 4 Accumulated Run Time | Details>Control>Clg>Stage4>C4RunTim | 29630
HEATING SETUP/STATUS
|  | Heating Enabled | Commission>Htg>HtgEn | 29707 | "YES" or "NO"
|  | Staged Heating Command | Details>Control>Htg>Status>StgHtgCmd | 29923 | 0% to 100%
|  | # Heating Stages | Details>Service>Factory>Standard>#HtgStgs | 29731 | 1 to 3
|  | Heating OAT Cutout Setpoint | Details>Control>Htg>Setup>HtgOATCutout-Sp | 29711 | 0 to 100 degrees
|  | Constant Volume Occupied Heating Setpoint | Details>Setpoints>CVHtgOcc-Sp | 29728 | Range 46 to 99 degrees
|  | Constant Volume Unoccuped Heating Setpoint | Details>Setpoints>CVHtgUnocc-Sp | 29729 | Range 45 to 98 degrees
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29739
|  | Heating Stage 1 Command | Details>Control>Htg>Stage1>H1 | 29732
|  | Heating Stage 1 Status | Details>Cotrol>Htg>Stage1>H1-S | 29735
|  | Heating Stage 2 Command | Details>Control>Htg>Stage2>H2 | 29733
|  | Heating Stage 2 Status | Details>Cotrol>Htg>Stage2>H2-S | 29736
|  | Heating Stage 3 Command | Details>Control>Htg>Stage3>H3 | 29734
|  | Heating Stage 3 Status | Details>Cotrol>Htg>Stage3>H3-S | 29737
|  | Supply Air Heating Limit Enabled | Detals>Control>Htg>Setup>SATHtgLimit-En | 29709 | "YES" or "NO"
|  | Supply Air Heating Limit Set point | Details>Control>Htg>Setup>SATHtgLimt-Sp | 29710 | 100 degree to 180 degree
ECONOMIZER SETUP/STATUS
|  | Economizer Enabled | Commission>Econ>Econ-En | 29747 | "YES" or "NO"
|  | Economizer Firware | Controller>SysCntrls>Econ>EconMainVer |  | View at board level or Map Gateway
|  | Economizer Damper Position | Details>Service>Inputs>Sensors>EconDampPos | 29748 | % open
|  | Economizer Minimum Position | Details>Control>Econ>Setup>Econ-MinPos | 29759 | % Open Set point
|  | Economizer OAT Set point | Details>Control>Econ>Setup>EconOAT-SpEn | 29753 | 40 to 80 degrees
|  | Economizer Free Cooling Available | Summary>Econ>Econ-Free | 29749 | "YES" or "NO"
|  | Economizer Mechanical Setup | Details>Control>Econ>Setup>EconMechStp | 29912 | Option B
|  | All Compressor OFF-Economizer | Details>Control>Clg>Setup>AllCompOff-Econ | 29584 | "YES" or "NO"
|  | Econ OA Enthalpy Setpoint | Details>Control>Econ>Setup>EconOAEth-Sp | 29754 | 10 to 50 BTU/Lb
|  | Free Cooling Selection | Details>Control>Econ>Setup>FreeClg-Sel | 29752 | Auto, Dry Bulb, Single or Dual Enthalpy
|  | Low Ambient Minimum Position | Details>Control>Econ>Setup>LowAmb-MinPos | 29756 | 0% to 100% econ damper open
|  | Low Ambient Set point | Details>Control>Econ>Setup>LowAmb-Sp | 29755 | 0 to 60 degrees
|  | Low Speed Fan Minimum Position | Details>Control>Econ>LowSpeedFan-MinPos | 29808 | 0% to 100% econ damper open
Power Exhaust Setup/STATUS
|  | Power Exhaust Fan Type | Details>Service>Factory>Econ>ExFType | 29774 | None, Non-Modualting, Modulating, VFD
|  | Power Exhaust Fan Command | Details>Control>PowerEx>Status> | 29775
|  | Power Exhaust Fan Status | Details>Control>PowerEx>Status>ExFan | 29777
|  | Power Exhaust Modulating Damper Output | Summary>PowerEx>EAD-O | 29782
|  | Building Pressure Set Point | Summary>PowerEx>Bldg-Sp | 29780
|  | Econ Damper Position Power Exhaust "OFF" | Summary>PowerEx>EconDmpPosFanOff | 29786
|  | Econ Damper Position Power Exhaust "ON" | Summary>PowerEx>EconDmpPosFanOn | 29785
|  | Power Exhaust Damper Position "OFF" | Commission>PoweEx>ExDmpPosFanOff | 29784
|  | Power Exhaust Damper Position "On" | Commission>PoweEx>ExDmpPosFanOn | 29783
|  | Power Exhaust VFD Output Status | Summary>PowerEx>ExFanVFD | 29776
CO2 Demand Ventilation Setup/STATUS
|  | (CO2) Demand Ventilation Mode | Commission>Dvent>Dvent-Mode | 29765 | Disabled, Controlled by IAQ, Diff Between IAQ & OAQ
|  | (CO2) Demand Ventilation Mode IAQ Set Point | Commission>Dvent>DventIAQ-Sp | 29767 | 0 to 5000 ppm
|  | (CO2) Demand Ventilation Max Econ Damper Position | Commission>Dvent>DVentMaxEconPos | 29766 | range 0% to 100% open
|  | (CO2) OAQ Range | Commission>Dvent>OAQRange | 29548 | 0 ppm to 5000 ppm
|  | (CO2) IAQ Range | Commission>Dvent>IAQRange | 29529 | 0 ppm to 5000 ppm
|  | (CO2) Demand Ventilation Differential Set Point | Commission>Dvent>DVentDiff-Sp | 29768 | 0 ppm to 5000 ppm
Sensor Inputs & Readings
|  | Supply Air Temperature | Details>Service>Inputs>Sensors>SAT | 29564
|  | Return Air Temperature | Details>Service>Inputs>Sensors>RAT | 29764
|  | Operational Outdoor Air Temperature | Details>Zone>Outdoor>OprOAT | 29541
|  | Operational Space Temperature | Details>Zone>Indoor>OprST | 29522
|  | Constant Volume Operating Heating Setpoint | Details>Setpoints>CVOprHtg-Sp | 29730
|  | Constant Volume Operating Cooling Setpoint | Details>Setpoints>OprCVClg-Sp | 29610
|  | Space Temperature Source | Details>Zone>Indoor>STsrc | 29523
|  | Space Humidity RAH input | Details>Control>Econ>Status>RAH | 29828
|  | Outdoor Air Humidity Input | Details>Service>Inputs>Sensor>OAH | N/A
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OA-Enth | 29545
|  | Return Air Enthalpy | Details>Control>Econ>Status>RA-Enth | 29763
|  | Outdoor Air Enthalpy | Details>Service>Inputs>Sensor>OAH-Enth | 29545
|  | Operational Space Humidity | Details>Zone>Indoor>OprSH | 29531
|  | Operational Outdoor Air Humidity | Details>Control>Econ>Status>OprOAH | 29544
|  | Net Override Space Temperature | Details>Service>Inputs>NetworkInputs>NetST | 29526 | Writable Point to Space Temp
|  | Net Override Outdoor Air Temperature | Details>Service>Inputs>NetworkInputs>NetOAT | 29543 | Writable Point to OAT
|  | Net Override Indoor Air Quality | Details>Service>Inputs>NetworkInputs>NetIAQ | 29530 | Writable Point to IAQ
|  | Net Override Outdoor Air Quality | Details>Service>Inputs>NetworkInputs>NetOAQ | 29549 | Writable Point to OAQ
|  | Net Override Outdoor Air Humidity | Details>Service>Inputs>NetworkInputs>NetOAH | 29546 | Writable Point to OAH
|  | Net Override Space Humidity | Details>Service>Inputs>NetworkInputs>NetSH | 29533 | Writable Point to Space Humidity
|  | Net Override Space Sensor Offset | Details>Service>Inputs>NetworkInputs>NetSSO | 29540 | Writable Point to Space Sensor offset
|  | Building Pressure | Summary>PowerEx>BldgPres | 29781 | (-).25 to .25"wc
|  | (CO2) IAQ Input | Details>Service>Inputs>Sensor>IAQ | N/A
|  | (CO2) OAQ Input | Details>Service>Inputs>Sensor>OAQ | N/A
HOT GAS REHEAT
|  | Hot Gas Reheat Enabled for Operation | Details>Service>Factory>Standard>HGR-En | 29789 | "YES" or "NO"
|  | Hot Gas Reheat Alternate Operation Enabled | Details>Control>HGR>HGRAlt-En | 29793 | "YES" or "NO"
|  | Hot Gas Reheat Gas Reheat Humidity Setpoint | Details>Control>HGR>HGRHum-SP | 29792 | 0% to 100%
|  | Hot Gas Reheat Alternate Operation Writable | Details>Control>HGR>HGRAltWrite | 29794 | "YES" or "NO"
|  | Hot Gas Reheat Enabled for Unoccupied Operation | Details>Control>HGR>HGRUnocc-En | 29904 | "YES" or "NO"
|  | Hot Gas Reheat Unoccupied Humidity Setpoint | Details>Control>HGR>HGRUnoccHum-Sp | 29903 | 0% to 100%
|  | Hot Gas Reheat Status | Details>Control>HGR>HGR-S | 29791
Note on B3: cedmonja: Used to identify each individual SSE board on the FC bus. When setting up for CCS Single Zone System. Address must be set from 18 thru 41 range to communicate on FC bus to System Manager system bus.
Note on B4: cedmonja: When the point is set to External the board will accept a command from bacnet point 29520 or 24VAC input into the SSE board OCC terminal. When set to Schedule the SSE board will operate according to the Internal Schedule set in the Map Gateway tool. When used with CCS OccMode is set to Schedule. This allows CCS to occ/unocc the unit.
Note on B5: cedmonja: This point will occupy and unoccupy the unit.
Note on B6: cedmonja: No- Commands the board to operate according to internal SSE board settings. On-Commands SSE board to operate according 24VAC inputs to SSE board T-stat terminals.
Note on B7: cedmonja: Wired Field Bus - sets board to communicate according to BACNET protocol. Note: When looking into Map Gateway tool it will show FC COM MODE. This the same as FC BUS MODE that is displayed on the board display.
Note on B8: cedmonja: Off-disables Single Zone VAV operation. On-Enables Single Zone VAV operation.
Note on B10: cedmonja: When using multiple SSE boards it maybe necessary to set the ID to a value of 6000 plus the Address. Example: Address is a value of 10 then the Device ID will be set to 6010.
Note on B16: cedmonja: Relearn-TRUE, Allows a discover of devices on the SA bus.
Note on B17: cedmonja: Displays if the unit is occupied or unoccupied.
Note on B18: cedmonja: "ON" allows a reset of alarms/Lockouts.
Note on B19: cedmonja: Operation: Self Test Sequencer steps through unit subsystems, one at a time, depending on what hardware options the control has been programmed with. See Table for the possible test, results. Each test has a stabilize period before energizing the corresponding equipment. Only during the Fan Test, is everything off or 0% actuated. All other tests, the FAN or VFD, are the only outputs ON during the stabilize period. Note: The control stops all current operation and begins the Fan test when you select Start from the Local UI. The Fan Test must prove airflow before proceeding with any other test. Table 6 (See Sequence of Operation Guide) shows the expected outputs for the Self Test. The shaded cells indicate the output turns during the self test. The control uses sensor feedback to verify the operation of the system while the equipment is being checked. Exceptions to the sensor feedback include: • If an APS and Duct Static Pressure Sensor are not installed, a prompt appears on the UI to check for FAN ON and airflow. • If OAT is within 2 degrees of SAT, the Economizer Test prompts the UI, for 10 minutes, for verification that the Economizer is opening (for example, Outdoor is 72°F, supply to space is 71°F). Visual inspection of the Economizer status is required. You can perform commands from the UI during the Self Test. The commands and control reactions to those commands are described in Table 7 (See Sequence of Operation Guide). Note: You can view the Test results throught the Map Gat
Note on B20: Chad Edmondson: By default "YES" the PID tuning parameters are managed by PRAC+(Pattern Recognition Adaptive Control) algorithm base on either Zone Temperature or Discharge Air Temperature process. PRAC+ can be turned off by changing the value of Cooling Adaptive Tuning Enable to "NO". Doing this will setup the PID to use the process defaults for either Zone Temperature or Discharge Temperature which can be found in the Cooling Adaptive Tuning chart attached to the right.
Note on B25: cedmonja: Variable speed- Sets the SSE board to operate as a VAV unit and control fan speed according to static pressure. Fixed Variable-Sets the SSE board to operate according to a 7 fan speed selection when the blower is VFD controlled. Single Speed-Sets the SSE Board to operate according to 100% fan operation. With no VFD applied to RTU.
Note on B26: cedmonja: None-Sets board not to recognize APS if not being used. Variable-allows operation of APS applied to a SSE VAV setup.
Note on B28: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B38: cedmonja: Yes-Prevents blower operation request from the start of 1 stage heat commmand until a 24VAC input is recognized at the MV pin and the FanOnDlyHeat expires. No-Ignores this operation.
Note on B39: cedmonja: This point is used to typically test blower operation or force blower only operation on during an unoccupied period.
Note on B41: cedmonja: Yes-Permits continuous fan operation when in occupied mode. No-Only permits fan during a call for heat or cool.
Note on B51: Chad Edmondson: #1 of circuits are set to 1 when used with a series 40 condensing unit. This will allow proper operation of high and low pressure switches.
Note on B52: cedmonja: At the initiation of each cooling demand the compressor with the lowest run hours energizes first. The compressor with the next number of lowest run hours energizes next, and so on. At the termination of the cooling demand, the compressor with the most run hours stage off in reverse order.
Note on B53: cedmonja: If lead lag is enabled. Hot Gas Bypass will operate in this sequence if set to "YES". VAV operation: If compressor operation is ongoing and C1 is not running, and fan speed drops below 50%, compressors stage off and stage back on in order. If fan speed is greater than 50% and the SAT is less than 45°F, the Lead/Lag function disables. CV operation: If the SAT is less than 45°F, the Lead/Lag function disables.
Note on B55: cedmonja: Setting to "YES" will prevent compressor operation below OAT Cooling Lockout Setpoint.
Note on B56: cedmonja: When Operational OAT falls below setpoint compressor operation will not be allowed.
Note on B57: cedmonja: If Cooling OAT Cutout Enble is Yes, the compressor is not permitted if the OAT is less than the cooling OAT Cutout. If Cooling OAT Cutout Enable is NO. the compressor cycles 10 minutes On and 5 minutes Off if the OAT is less than the LowAmb10On5Off Setpoint. If a compressor is in the 10 min On cycle and the evaportator temperature (EC1 thru EC4) drops below 26 degrees F. the compressor output de-endergizes and the 5 minute ASCD starts. After 5 minutes ASCD expires, the compressor ouput is permitted. Anytime the compressor output de-energizes due to the evaporator coil temperature protection it does not count towards a hard compressor lockout.
Note on B61: cedmonja: Yes does not permit compressor output if SAT falls below SATCoolLimit-SP. No Permits compressor output at any SAT.
Note on B84: cedmonja: Setpoint does not allow heating operation when Operational OAT goes above the setpoint.
Note on B98: cedmonja: Yes-enables economizer function. No-disables economizer function.
Note on B100: cedmonja: Value displays % economizer damper is open.
Note on B101: cedmonja: Economizer damper minimum % open setpoint during occupied mode.
Note on B102: cedmonja: Dry bulb economizer setpoint. When OAT drops below set point economizer functions starts.
Note on B103: cedmonja: Yes-Economizer free cooling is available. No-Economizer free cooling is not available.
Note on B104: cedmonja: Option A-(Do Not Use) Economizer damper position and/or time triggers compressor operation to supplement free cooling. Option B- Supply air temperature with VAV supply air temperature(upper/lower) setpoint triggers compressor operation to supplement free cooling.
Note on B105: cedmonja: Yes-Does not allow compressor operation during free cooling. No-allows compressor operation durig free cooling.
Note on B106: cedmonja: Single enthalpy free cooling setpoint. When Outside Air Enthalpy is below setpoint free cooling is available.
Note on B115: cedmonja: With the series 10 & 20 RTU the only curren option is Non-Modulating Power Exhaust.
Note on B127: cedmonja: Demand Ventilation mode selection. Disabled-No Demand Ventilation Function. Controlled by IAQ- Enables Demand Ventilation control with IAQ input. Differential between IAQ & OAQ- Enables Demand Ventilation control with a comparison between IAQ & OAQ.
Note on B131: cedmonja: IAQ sensor range.
Note on B139: cedmonja: This point will reflect the offset + or - range of the occupied heating setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B140: cedmonja: This point will reflect the offset + or - range of the occupied cooling setpoint when using a space sensor wired to the ST,Com & SSO terminal.
Note on B161: cedmonja: Normal Occupied Operation Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 output energizes and the AUX-HGR output energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 output energizes but the AUX-HGR output de-energizes. Any additional cooling demands energize compressor outputs, but do not change the status of the AUX-HGR output. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas
Note on B162: cedmonja: Alternate Mode: If the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, and no demand for cooling, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for one stage of cooling and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and AUX-HGR outputs energize, and C2 energizes. If there is a demand for both first and second cooling stages and the return humidity is greater than or equal to the Hot Gas Reheat Humidity Setpoint, C1 and C2 outputs energize and AUX-HGR de-energizes. The unit can operate in reheat mode if the economizer is operating in free cooling mode. Note: If HGR Enabled for Unoccupied Operation is enabled, during unoccupied mode the HGR Unoccupied Humidity Setpoint is used in place of Hot Gas Reheat Humidity Setpoint.
Note on B164: cedmonja: YES- Allows access to hot gas reheat moode selection in HGRAlt-En. NO-Does not allow access to hot gas reheat mode selection in HGRAlt-En.
Note on B165: cedmonja: YES- Allows hot gas reheat operation when occupancy status is Unoccupied. NO- Does not allow hot has reheat operation when occupancy status is Unoccupied.

## Alarms
Severity | Alarm | How to get it
Critical | C1 Locked Out Due to High Pressure | Three HPS1 trips within one hour
| C2 Locked Out Due to High Pressure | Three HPS2 trips within one hour
| C3 Locked Out Due to High Pressure | Three HPS3 trips within one hour
| C4 Locked Out Due to High Pressure | Three HPS4 trips within one hour
| C1 Locked Out Due to Low Pressure | Three LPS1 trips within one hour
| C2 Locked Out Due to Low Pressure | Three LPS2 trips within one hour
| C3 Locked Out Due to Low Pressure | Three LPS3 trips within one hour
| C4 Locked Out Due to Low Pressure | Three LPS4 trips within one hour
| C1 Locked Out Due to Coil Freeze | Three FS1 trips within one hour (Evap Coil Temp < Evap Coil Temp Cutout SP)
| C2 Locked Out Due to Coil Freeze | Three FS2 trips within one hour (Evap Coil Temp < Evap Coil Temp Cutout SP)
| C3 Locked Out Due to Coil Freeze | Three FS3 trips within one hour (Evap Coil Temp < Evap Coil Temp Cutout SP)
| C4 Locked Out Due to Coil Freeze | Three FS4 trips within one hour (Evap Coil Temp < Evap Coil Temp Cutout SP)
| Exhaust Fan VFD Failure | EX VFD BI trips (must be set up as Exhaust must be setup as Variable Frequency Fan)
| HS1 Locked Out Due to Limit Switch | Three LS1 trips within one hour
| HS2 Locked Out Due to Limit Switch | Three LS2 trips within one hour
| HS3 Locked Out Due to Limit Switch | Three LS3 trips within one hour
| Unit Shutdown Due to Smoke, etc | SD input loses 24 VAC to it
| Supply Fan VFD Failure | Fan VFD Input trips (must be set up as NOT Single Speed)
| No Heat-Cool Due to Unreliable Space-T | Input Unreliable
| 4-Stage Communication Failure | Four stage board goes from Online -> Offline
| Economizer Communication Failure | Economizer board goes from Online -> Offline
| Outputs Disabled Due to Low Input V | Blackout Conditions
| Outputs Limited Due to Brownout Input V | Brownout Conditions
| Unit Locked Out Due to APS | Three APS trips with 1.5 hours (if APS is installed OR based on Duct Pressure if Variable Speed Fan)
| Unit Locked Out Due to Supply Fan OL | Three FAN OVR trips within one hour
| Unit Locked Out Due to High Duct-P | Duct Static Pressure > High Duct Static Pressure Setpoint
Service Priority | Evaporator Coil Temp 1 Sensor Failure | Input unreliable and Number of Cooling Stages >= 1
| Condenser Coil Temp 1 Sensor Failure | Input unreliable and Number of Cooling Stages >= 1
| Evaporator Coil Temp 2 Sensor Failure | Input unreliable and Number of Cooling Stages >= 2
| Condenser Coil Temp 2 Sensor Failure | Input unreliable and Number of Cooling Stages >= 2
| Evaporator Coil Temp 3 Sensor Failure | Input unreliable and Number of Cooling Stages >= 3
| Condenser Coil Temp 3 Sensor Failure | Input unreliable and Number of Cooling Stages >= 3
| Evaporator Coil Temp 4 Sensor Failure | Input unreliable and Number of Cooling Stages >= 4
| Condenser Coil Temp 4 Sensor Failure | Input unreliable and Number of Cooling Stages >= 4
| Building Pressure Sensor Failure | Input unreliable
| Outdoor Air Temperature Sensor Failure | Input Unreliable
| Return Air Temperature Sensor Failure | Input Unreliable and Variable Speed Fan
| Supply Air Temperature Sensor Failure | Unreliable AND (Econ Comm Status = Online OR Mixed Air Sequencer = DAT Control)
| Unit Shutdown Due to Supply Fan Overload | FAN OVR Trip (but less than three in one hour as that would cause 'Unit Locked Out Due to Supply Fan OL')
| Main Controller Calibration Error | Missing Cal Data
| FDDM Controller Calibration Error | Missing Cal Data
| Econ Controller Caliabration Error | Missing Cal Data
| 4 Stage Controller Calibration Error | Missing Cal Data
| Unit Shutdown Due to Air Proving Switch | APS trip (but less than three in 1.5 hours as that would cause 'Unit Locked Out Due to APS')
| FDDS Controller Calibration Error | Missing Cal Data
Service | Duct Pressure Sensor Failure | Input Unreliable and Variable Speed Fan
| Return Air Humidity Sensor Failure | Input unreliable
| Outdoor Air Humidity Sensor Failure | Input unreliable
| Supply Humidity Sensor Failure | Input unreliable
| Indoor Air Quality Sensor Failure | Input unreliable
| Outdoor Air Quality Sensor Failure | Input unreliable
| Fresh Air Intake Sensor Failure | Input unreliable
| Mixed Air Temp Sensor Failure | Input unreliable
| Space Indoor Temp Sensor Failure | Input unreliable
| Space Offset Sensor Failure | Input unreliable
| C1 Shutdown Due to High Pressure | HPS1 Trip
| C2 Shutdown Due to High Pressure | HPS2 Trip
| C3 Shutdown Due to High Pressure | HPS3 Trip
| C4 Shutdown Due to High Pressure | HPS4 Trip
| C1 Shutdown Due to Low Pressure | LPS1 Trip
| C2 Shutdown Due to Low Pressure | LPS2 Trip
| C3 Shutdown Due to Low Pressure | LPS3 Trip
| C4 Shutdown Due to Low Pressure | LPS4 Trip
| C1 Shutdown Due to Coil Freeze | FS1 Trip (Evap Coil Temp < Evap Coil Temp Cutout SP)
| C2 Shutdown Due to Coil Freeze | FS2 Trip (Evap Coil Temp < Evap Coil Temp Cutout SP)
| C3 Shutdown Due to Coil Freeze | FS3 Trip (Evap Coil Temp < Evap Coil Temp Cutout SP)
| C4 Shutdown Due to Coil Freeze | FS4 Trip (Evap Coil Temp < Evap Coil Temp Cutout SP)
| Low Outdoor Air Temp Cooling Cutout | OAT < OAT Cooling Cutout
| Econ Economizing When It Should Not | Economizer > Min OA Position + Tolerance
| Econ Not Economizing When It Should | Economizer < Min OA Position + Tolerance
| Economizer Damper Not Modulating | ABS(Economizer - Feedback) > Damper Pos Error
| Economizer Letting In Excess Outdoor Air | (Economizer > Min OA Position + Tolerance AND Ramp Min OA) OR (Economizer > Tolerance AND Ramp Closed)
| HS1 Shutdown Due to Limit Switch | LS1 Trip
| HS2 Shutdown Due to Limit Switch | LS2 Trip
| HS3 Shutdown Due to Limit Switch | LS3 Trip
| HS1 Off Due to Gas Valve | GV1 Lost Proof
| HS2 Off Due to Gas Valve | GV2 Lost Proof
| HS3 Off Due to Gas Valve | GV3 Lost Proof
| Dirty Filter | DFS Trip
| FDD 1 Communication Failure | FDD Master Online -> Offline
| FDD 2 Communication Failure | FDD Slave Online -> Offline
| Unit has Received a Purge Request | PURGE-S on Econ trip
| Excessive Supply Air Temp Cooling | SAT < Excessive SAT Cooling Sp
| HS1 Gas Valve Failure | GV1 False Proof
| HS2 Gas Valve Failure | GV2 False Proof
| HS3 Gas Valve Failure | GV3 False Proof
| Excessive Supply Air Temp Heating | SAT > Excessive SAT Heating SP
| Space Temperature Cooling Alarm | Space Temp > Operating Cooling SP for more than 60 minutes
| C1 Refrigerant Low | FDD Alarm
| C2 Refrigerant Low | FDD Alarm
| C3 Refrigerant Low | FDD Alarm
| C4 Refrigerant Low | FDD Alarm
| C1 Excessive Refrigerant Flow | FDD Alarm
| C2 Excessive Refrigerant Flow | FDD Alarm
| C3 Excessive Refrigerant Flow | FDD Alarm
| C4 Excessive Refrigerant Flow | FDD Alarm
| C1 Inefficient Compressor | FDD Alarm
| C2 Inefficient Compressor | FDD Alarm
| C3 Inefficient Compressor | FDD Alarm
| C4 Inefficient Compressor | FDD Alarm
| C1 Refrigerant Flow Restriction | FDD Alarm
| C2 Refrigerant Flow Restriction | FDD Alarm
| C3 Refrigerant Flow Restriction | FDD Alarm
| C4 Refrigerant Flow Restriction | FDD Alarm
| C1 High Side Heat Transfer Problem | FDD Alarm
| C2 High Side Heat Transfer Problem | FDD Alarm
| C3 High Side Heat Transfer Problem | FDD Alarm
| C4 High Side Heat Transfer Problem | FDD Alarm
| C1 Low Side Heat Transfer Problem | FDD Alarm
| C2 Low Side Heat Transfer Problem | FDD Alarm
| C3 Low Side Heat Transfer Problem | FDD Alarm
| C4 Low Side Heat Transfer Problem | FDD Alarm
| C1 Reduce Evaporator Airflow | FDD Alarm
| C2 Reduce Evaporator Airflow | FDD Alarm
| C3 Reduce Evaporator Airflow | FDD Alarm
| C4 Reduce Evaporator Airflow | FDD Alarm
| C1 Add Charge | FDD Alarm
| C2 Add Charge | FDD Alarm
| C3 Add Charge | FDD Alarm
| C4 Add Charge | FDD Alarm
| C1 Insufficient Refrigerant Flow | FDD Alarm
| C2 Insufficient Refrigerant Flow | FDD Alarm
| C3 Insufficient Refrigerant Flow | FDD Alarm
| C4 Insufficient Refrigerant Flow | FDD Alarm
| C1 Recover Charge | FDD Alarm
| C2 Recover Charge | FDD Alarm
| C3 Recover Charge | FDD Alarm
| C4 Recover Charge | FDD Alarm
| C1 Non-Condensables Present | FDD Alarm
| C2 Non-Condensables Present | FDD Alarm
| C3 Non-Condensables Present | FDD Alarm
| C4 Non-Condensables Present | FDD Alarm
| C1 Liquid Temp Greater Than Cond Temp | FDD Alarm
| C2 Liquid Temp Greater Than Cond Temp | FDD Alarm
| C3 Liquid Temp Greater Than Cond Temp | FDD Alarm
| C4 Liquid Temp Greater Than Cond Temp | FDD Alarm
| Hot H2o FS Open to Prevent Coil Freeze | Hydronic Heating Enabled AND ((HW FREEZE BI trip AND Unreliable OAT) OR (HW FREEZE BI trip AND OAT < 40degF)
| Hot H2o FS Opened When It Should Not | Hydronic Heating Enabled AND OAT > 40degF AND HW FREEZE BI trip
| Space Temperature Heating Alarm | Space Temp < Operating Heating SP for more than 60 minutes
| Not Economizing - No Supply Air Sensor | (Free Cooling Available AND MA Sequencer = DAT Control AND SAT Unreliable) OR (SAT Unreliable AND MA Sequencer = Zone Control AND MA State = Mech AND Free Cooling Available) OR (Tstat Only AND Mech AND Free Cooling Available)
| Using Return Instead of Space Temp | Effective Zone Source = Return Air Temp AND NOT Tstat Only
| Air Proving Switch is Stuck Closed | APS is closed, but fan command is not given
| C1 Basic Data Not Available | FDD Alarm
| C2 Basic Data Not Available | FDD Alarm
| C3 Basic Data Not Available | FDD Alarm
| C4 Basic Data Not Available | FDD Alarm
| C1 Unit Off | FDD Alarm
| C2 Unit Off | FDD Alarm
| C3 Unit Off | FDD Alarm
| C4 Unit Off | FDD Alarm
| C1 Return Air Wet-Bulb Temp Out Of Range | FDD Alarm
| C2 Return Air Wet-Bulb Temp Out Of Range | FDD Alarm
| C3 Return Air Wet-Bulb Temp Out Of Range | FDD Alarm
| C4 Return Air Wet-Bulb Temp Out Of Range | FDD Alarm
| C1 Ambient Temp Too Low | FDD Alarm
| C2 Ambient Temp Too Low | FDD Alarm
| C3 Ambient Temp Too Low | FDD Alarm
| C4 Ambient Temp Too Low | FDD Alarm
| C1 Ambient Temp Too High | FDD Alarm
| C2 Ambient Temp Too High | FDD Alarm
| C3 Ambient Temp Too High | FDD Alarm
| C4 Ambient Temp Too High | FDD Alarm
| C1 Return Air Wet-Bulb Temp Too Low | FDD Alarm
| C2 Return Air Wet-Bulb Temp Too Low | FDD Alarm
| C3 Return Air Wet-Bulb Temp Too Low | FDD Alarm
| C4 Return Air Wet-Bulb Temp Too Low | FDD Alarm
| C1 Return Air Wet-Bulb Temp Too High | FDD Alarm
| C2 Return Air Wet-Bulb Temp Too High | FDD Alarm
| C3 Return Air Wet-Bulb Temp Too High | FDD Alarm
| C4 Return Air Wet-Bulb Temp Too High | FDD Alarm
| C1 Condensing Temp Less Than Ambient | FDD Alarm
| C2 Condensing Temp Less Than Ambient | FDD Alarm
| C3 Condensing Temp Less Than Ambient | FDD Alarm
| C4 Condensing Temp Less Than Ambient | FDD Alarm
| C1 Suction Temp Less Than Evap Temp | FDD Alarm
| C2 Suction Temp Less Than Evap Temp | FDD Alarm
| C3 Suction Temp Less Than Evap Temp | FDD Alarm
| C4 Suction Temp Less Than Evap Temp | FDD Alarm
| C1 Evap Temp Greater Than Ambient Temp | FDD Alarm
| C2 Evap Temp Greater Than Ambient Temp | FDD Alarm
| C3 Evap Temp Greater Than Ambient Temp | FDD Alarm
| C4 Evap Temp Greater Than Ambient Temp | FDD Alarm
| C1 Liquid Temp Less Than Ambient Temp | FDD Alarm
| C2 Liquid Temp Less Than Ambient Temp | FDD Alarm
| C3 Liquid Temp Less Than Ambient Temp | FDD Alarm
| C4 Liquid Temp Less Than Ambient Temp | FDD Alarm
| C1 Invalid Suction or Ambient Temp | FDD Alarm
| C2 Invalid Suction or Ambient Temp | FDD Alarm
| C3 Invalid Suction or Ambient Temp | FDD Alarm
| C4 Invalid Suction or Ambient Temp | FDD Alarm
| C1 Invalid RA Dry-Bulb or Wet-Bulb Temp | FDD Alarm
| C2 Invalid RA Dry-Bulb or Wet-Bulb Temp | FDD Alarm
| C3 Invalid RA Dry-Bulb or Wet-Bulb Temp | FDD Alarm
| C4 Invalid RA Dry-Bulb or Wet-Bulb Temp | FDD Alarm
| C1 Invalid Liquid and Suction Pressure | FDD Alarm
| C2 Invalid Liquid and Suction Pressure | FDD Alarm
| C3 Invalid Liquid and Suction Pressure | FDD Alarm
| C4 Invalid Liquid and Suction Pressure | FDD Alarm
| C1 Invalid Suction Temp | FDD Alarm
| C2 Invalid Suction Temp | FDD Alarm
| C3 Invalid Suction Temp | FDD Alarm
| C4 Invalid Suction Temp | FDD Alarm
| C1 Invalid Liquid and Suction Temp | FDD Alarm
| C2 Invalid Liquid and Suction Temp | FDD Alarm
| C3 Invalid Liquid and Suction Temp | FDD Alarm
| C4 Invalid Liquid and Suction Temp | FDD Alarm
| C1 Return Air Dry-Bulb Temp Too Low | FDD Alarm
| C2 Return Air Dry-Bulb Temp Too Low | FDD Alarm
| C3 Return Air Dry-Bulb Temp Too Low | FDD Alarm
| C4 Return Air Dry-Bulb Temp Too Low | FDD Alarm
| C1 Return Air Dry-Bulb Temp Too High | FDD Alarm
| C2 Return Air Dry-Bulb Temp Too High | FDD Alarm
| C3 Return Air Dry-Bulb Temp Too High | FDD Alarm
| C4 Return Air Dry-Bulb Temp Too High | FDD Alarm
| C1 EI Below 75% Expected Performance | FDD Alarm
| C2 EI Below 75% Expected Performance | FDD Alarm
| C3 EI Below 75% Expected Performance | FDD Alarm
| C4 EI Below 75% Expected Performance | FDD Alarm
| C1 CI Below 75% Expected Performance | FDD Alarm
| C2 CI Below 75% Expected Performance | FDD Alarm
| C3 CI Below 75% Expected Performance | FDD Alarm
| C4 CI Below 75% Expected Performance | FDD Alarm
| C1 EI+CI Below 75% Expected Performance | FDD Alarm
| C2 EI+CI Below 75% Expected Performance | FDD Alarm
| C3 EI+CI Below 75% Expected Performance | FDD Alarm
| C4 EI+CI Below 75% Expected Performance | FDD Alarm
| C1 FDD Not Functioning Sensor Unreliable | FDD Alarm
| C2 FDD Not Functioning Sensor Unreliable | FDD Alarm
| C3 FDD Not Functioning Sensor Unreliable | FDD Alarm
| C4 FDD Not Monitoring Sensor Unreliable | FDD Alarm
| C1 FDD Not Monitoring Conditions | FDD Alarm
| C2 FDD Not Monitoring Conditions | FDD Alarm
| C3 FDD Not Monitoring Conditions | FDD Alarm
| C4 FDD Not Monitoring Conditions | FDD Alarm
| C1 FDD Not Monitoring Equipment Data | FDD Alarm
| C2 FDD Not Monitoring Equipment Data | FDD Alarm
| C3 FDD Not Monitoring Equipment Data | FDD Alarm
| C4 FDD Not Monitoring Equipment Data | FDD Alarm

## Heat Pump Split Wiring
J07PC Wiring
J10PC Wiring
J15PC Wiring
J20PD Wiring

## J07YC-J12YDWiring
J07YCC Model Wiring
J10YCC to J12YCC Model Wiring
J10YD to J12YD Wiring
J15YD to J20YD Wiring

## J30-50YDWiring
460/575 VAC Wiring
208/230 VAC Wiring

## SSESeries20RTUReheatWiring
Note: Select View at Top of file and Zoom to see wire and notation information better.

## Parts
model list made from J07ZJN10V5BZZ70001 575VAC RTU for Conversion
Source One Part Number | Quantity | Description | SAP |  |  | C-Spec link
S1-02546665000 | 1 | HARNESS,WIRE,S1,UCB | 112847 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128427 A&Type=Part&SrchVal=1128427&Record=0&Sel=Act
S1-02546666000 | 1 | HARNESS,WIRE,S2,UCB | 1128428 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128428 A&Type=Part&SrchVal=1128428&Record=0&Sel=Act
S1-02546670000 | 1 | HARNESS,WIRE,S3,UCB,GH,TWO STAGE | 1128482 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128482 D&Type=Part&SrchVal=1128482&Record=0&Sel=Act
S1-02546755000 | 1 | HARNESS,WIRE,S4,UCB | 1128484 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128484 A&Type=Part&SrchVal=1128484&Record=0&Sel=Act
S1-02546757000 | 1 | HARNESS,WIRE,S5,UCB | 1128486 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128486 A&Type=Part&SrchVal=1128486&Record=0&Sel=Act
S1-02546761000 | 1 | HARNESS,WIRE,S9,UCB,TWO STAGE,VFD | 1128490 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128490 B&Type=Part&SrchVal=1128490&Record=0&Sel=Act
S1-02546766000 | 1 | HARNESS,WIRE,S10,UCB,W/M4 | 1128505 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128505 A&Type=Part&SrchVal=1128505&Record=0&Sel=Act
S1-02546767000 | 1 | HARNESS,WIRE,P11,RAT/SAT | 1128506 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128506 A&Type=Part&SrchVal=1128506&Record=0&Sel=Act
S1-02546768000 | 1 | HARNESS,WIRE,S13,SMOKE DETECTOR | 1128507 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128507 A&Type=Part&SrchVal=1128507&Record=0&Sel=Act
S1-02546769000 | 1 | HARNESS,WIRE,S15,UCB-ECON | 1128508 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128508 A&Type=Part&SrchVal=1128508&Record=0&Sel=Act
S1-02546772000 | 1 | HARNESS,WIRE,S17,ECON | 1128511 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128511 A&Type=Part&SrchVal=1128511&Record=0&Sel=Act
S1-02546773000 | 1 | HARNESS,WIRE,S20,ECON | 1128512 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128512 A&Type=Part&SrchVal=1128512&Record=0&Sel=Act
S1-02546776000 | 1 | HARNESS,WIRE,S22,UCB,APS/DFS | 1128515 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1128515 A&Type=Part&SrchVal=1128515&Record=0&Sel=Act
S1-02527729700 | 1 | TRNSF,575,24,75VA,50/60HZ | 7790 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C071B&Part=025-27729-000C/ 7790&Type=Part&SrchVal=27729&Record=0&Sel=Act
S1-03109130000 | 3 | SENSOR,TEMP,OUTSIDE/RETURN/SUPPLY AIR | 66194 | 2958465 | HEAT SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C101&Part=031-09130-000A/ 66194&Type=Part&SrchVal=9130&Record=1&Sel=Act
S1-03103026000 | 2 | SENSOR,TEMPERATURE,6 INCH LEAD | 1040725 | 2958465 | HEAT SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C101&Part=031-03026-000A/ 1040725&Type=Part&SrchVal=3026&Record=9&Sel=Act
S1-02436103000 | 1 | CONTROLLER,VFD,E560,3HP 575V | 990171 | 2958465 | INSTALL OPTIONS/ACCESSORIES/IAQ | http://c4445m012/cspecs/SinglePart.asp?Spec=C160F&Part=024-36103-000A/ 990171&Type=Part&SrchVal=36103&Record=0&Sel=Act
SAP# 1154013 | 1 | Economizer Controller, Firmware 3.0.0.1072 | 1154013 |  |  | http://c4445m012/cspecs/SinglePart.asp?Spec=C159&Part=1154013 B&Type=Vendor_Part&SrchVal=SE-ECO1001&Record=1&Sel=Act
|  | Economizer/downflow |  |  |  | http://c4445m012/cspecs/SinglePart.asp?Spec=C194NA&Part=1149241 A&Type=Part&SrchVal=1149241&Record=0&Sel=Act
S1-03103031000 | 1 | BOARD,CNTRL,SES,2 STAGE,W/ COMM,UCB2 | 1089070 | 2958465 | ELECTRICAL SECTION | http://c4445m012/cspecs/SinglePart.asp?Spec=C160C&Part=031-03031-000A/ 1089070&Type=Part&SrchVal=03031&Record=0&Sel=Act
Under Construction

## Parts1
C-Spec Link
| 1056893 | 1 | HARNESS, WIRING, S1, UCB | 2014-08-18 | 2958465 | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1056893 A&Type=Part&SrchVal=1056893&Record=0&Sel=Act
| 1056894 | 1 | HARNESS, WIRING, S2 | 2014-10-06 | 2958465 | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1056894 A&Type=Part&SrchVal=1056894&Record=0&Sel=Act
| 1056895 | 1 | HARNESS, WIRING, S4, W/VFD | 2014-10-06 | 2958465 | http://c4445m012/cspecs/SinglePart.asp?Spec=C172D&Part=1056895 A&Type=Part&SrchVal=1056895&Record=0&Sel=Act
| 1056896 | 1 | HARNESS, WIRING, S22 | 2014-10-06 | 2958465
| 1056897 | 1 | HARNESS, WIRING, S5 | 2014-08-01 | 2958465
| 1056899 | 1 | HARNESS, WIRING, S30 | 2014-08-18 | 2958465
| 1056900 | 1 | HARNESS, WIRING, S31 | 2014-11-07 | 2958465
| 1057041 | 1 | HARNESS, WIRING, SA BUS, ECON | 2014-10-06 | 2958465
| 1065043 | 1 | HARNESS, WIRING, SA BUS, UCB | 2014-08-18 | 2958465
| 1065046 | 1 | HARNESS, WIRING, S27 | 2014-10-06 | 2958465
| 1065069 | 1 | HARNESS, WIRING, S16 | 2014-07-25 | 2958465
| 1065070 | 1 | HARNESS, WIRING, S17/S18 | 2014-08-18 | 2958465
| 1065077 | 1 | HARNESS, WIRING, S7 | 2014-08-18 | 2958465
| 1066804 | 2 | HARNESS, WIRING, P17/18 | 2014-08-18 | 2958465
| 1066979 | 1 | HARNESS, WIRING, S10, REHEAT | 2014-08-18 | 2958465
| 1067061 | 1 | HARNESS, WIRING, P29 | 2014-11-07 | 2958465
| 1067065 | 1 | HARNESS, WIRING, S14 | 2014-11-07 | 2958465
| 1067066 | 1 | HARNESS, WIRING, S8 | 2014-11-07 | 2958465
| 1111267 | 1 | Harness, Wiring, S9, VFD | 2014-10-06 | 2958465
| 1183591 | 1 | HARNESS WIRING, S3, GAS HEAT | 2014-12-19 | 2958465
Econ Actuator:
Under Construction