## Piping Program
|  | LIQUID LINE CALCULATIONS |  |  |  |  | R410A | CALCULATOR |  |  |  | JOB NAME_______________________
| VERT. HT |  |  | TOTAL | UNIT | FRICTION | TOTAL | LIQ. | LIQ |  |  | UNIT NUMBER____________________
LINE | + DROP | NUMBER | ACT. | EQU | SIZE | LOSS | PRESS | LINE | LINE
SIZE | - RISE | ELBOWS | length | length | MBH | PSI | LOSS | CHARGE OZ. | VELOCITY |  |  | MODEL___________________________
1/4 | 0 | 8 | 330 | 30 | 180 | 679.628 | 679.628 | 63.9078 | 3884.945
5/16 | 0 | 8 | 330 | 336.4 | 180 | 1717.6072 | 1717.6072 | 111.144 | 2271.0975
3/8 | 0 | 8 | 330 | 337.2 | 180 | 627.9885 | 627.9885 | 172.2732 | 1450.1325
1/2 | 0 | 8 | 330 | 339.6 | 180 | 140.7897 | 140.7897 | 311.2032 | 758.586 |  | Liquid line maximum Velocity 400 fpm Liquid Minimum is 125 fpm
5/8 | 0 | 8 | 330 | 342 | 180 | 43.092 | 43.092 | 502.9266 | 472.1445 |  | Total Liquid Line pressure drop cannot exceed 50 psig
3/4 | 0 | 8 | 330 | 342.8 | 180 | 17.14 | 17.14 | 741.8862 | 316.197
7/8 | 0 | 8 | 330 | 344.4 | 180 | 7.496 | 7.496 | 1039.1964 | 227.6475 |  |  | HEAT PUMP: Norman Heat Pump Condensing Units have a factory
1 1/8 | 0 | 8 | 330 | 349.2 | 180 | 2.0342 | 2.0342 | 1733.8464 | 133.4815 | N0TE 1 | Installed Suction Accumulator. Limit lines to 75 feet | Installed Suction Accumulator sized for no more than 75 foot of lines.
1 3/8 | 0 | 8 | 330 | 355.6 | 180 | 0.72008 | 0.72008 | 2636.8914 | 87.6532 |  |  | Limit Liquid Line loss to no more than 11 psig
1 5/8 | 0 | 8 | 330 | 360.4 | 180 | 0.30991 | 0.30991 | 3720.5454 | 61.901 |  |  | Extended Lines may cause Accumulator Replacement
2 1/8 | 0 | 8 | 330 | 371.6 | 180 | 0.085556 | 0.085556 | 6495.2554 | 35.611 |  |  | Call Application Department
2 5/8 | 0 | 8 | 330 | 382 | 180
3 1/8 | 0 | 8 | 330 | 394
3 5/8 | 0 | 8 | 330 | 410
4 1/8 | 0 | 8 | 330 | 426
SUCTION LINE CALCULATIONS
NOTE 2
[5 empty] | TOTAL | UNIT | FRICTION |  | SUCT.
|  | LINE | NO. | ACT. | EQU. | SIZE | LOSS | REF. | LINE |  |  | Suction Maximum Velocity is 3000 FPM
|  | SIZE | ELBOWS | length | length | MBH | PSI | VELOCITY | CHARGE OZ. |  |  | Minimum Velocity Vertical Suction Line Riser 1000 FPM
|  | 1/2 | 8 | 330 | 339.6 | 180 | 2783.0775 | 20832.75 | 9.5304 |  |  | Minimum Horizontal Velocity Suction line is 800 FPM
|  | 5/8 | 8 | 330 | 342 | 180 | 943.3185 | 12954.375 | 19.0608 | note 3 total liquid line pressure drop cannot exceed 50psi
|  | 3/4 | 8 | 330 | 342.8 | 180 | 322.6704 | 8807.4643 | 28.5912 |  |  | total suction line pressure drop cannot exceed
|  | 7/8 | 8 | 330 | 344.4 | 180 | 153.3045 | 6228.675 | 38.1216 |  |  | 5 lb pd. Each pound above 5 = approx 1% capacity loss
|  | 1-1/8 | 8 | 330 | 349.2 | 180 | 42.7463 | 3637.8 | 66.7128
|  | 1-3/8 | 8 | 330 | 355.6 | 180 | 15.368 | 3420 | 99.1162
|  | 1-5/8 | 8 | 330 | 360.4 | 180 | 6.5683 | 1692 | 144.9288
|  | 2-1/8 | 8 | 330 | 371.6 | 180 | 2.3708 | 951.75 | 266.8512
|  | 2-5/8 | 8 | 330 | 382 | 180 | 0.61798 | 634.5 | 396.4646
|  | 3-1/8 | 8 | 330 | 385.2 | 180 | 0.27263 | 465.3 | 579.4483
|  | 3-5/8 | 8 | 330 | 386.8 | 180 | 0.02018 | 444.15 | 785.305
|  | 4-1/8 | 8 | 330 | 388.4 | 180 | 0.0090872 | 237.9375 | 1029.2832
DATE________________ |  | NO.: DISTRIBUTOR________________________________________; LOSS: Requested By________________________________
CONDENSING UNIT LOCATION_____________ |  | ACT.: EVAP/BLOWER LOCATION_______________; LOSS: HEIGHT DIFFERENCE________________________
REFRIGERANT CHARGE FOR UNIT & COIL______________________ |  | EQU.: CHARGE FOR LINES________________; REF.: EST TOTAL CHARGE_________________
REFRIGERANT SPECIALTIES SUGGESTED: |  | EQU.: ORIFICE CHANGE_____________; REF.: ADD TXV___________________
SCHRADER CONNECTION IN LIQUID LINE AT COIL________________
ACCUMULATOR TO HOLD _________ |  | EQU.: CONNECTIONS TO BE ___________________
ADD SIGHT GLASS AT AT CONDENSING UNIT AS WELL AS AT THE EVAPORATOR COIL________________
ADD PRESSURE TAP AT THE COIL'S LIQUID LINE AND SUCTION LINE IN THE HORIZONTAL LINES _________
| #1 UNIT GEOGRAPHY CONDENSOR ABOVE EVAPORATOR | SIZE: #2 EVAPORATOR ABOVE CONDENSOR
#3 CONDENSOR AND EVAPORATOR ON SAME LEVEL

## Engineering Data
There is a limit of how far you can pipe refrigerant lines. Always use the shortest distance and if over 125 feet phone a friend
Caution: Factory matched Condensing units with a Solutions or UPG AHRI rated air handler using a Tandem Compressor
recommend an oil separator insulated with heater when line sets are over 125 feet. {4 pipe CU's}. See Temprite Coalesent style
Caution: Condensing units with a tandem compressor with a 3rd party coil are required to use an Oil Separator if over 100 ft lines
Caution: It is recommended to use an Oil Separator on all single compressors when line sets are over 125 feet.
Oil Separators are field supplied and field installed. See Temprite Coalesent models. Call Application Department
Liquid Line maximum 400 FPM Velocity and above the minimum of 125 FPM to ensure proper operation and longevity
Liquid line total pressure drop cannot exceed 50 PSIG
Suction gas minimum velocity of 1000 fpm for R410a is required for oil return up a vertical riser
Suction gas minimum velocity above 800 fpm for Horizontal lines {recommend 1000 FPM to be safe}.
Total suction line pressure drop cannot exceed 5 lb. Above 5 psig = prox 1% capacity loss
To prevent noise 3000 fpm is the maximum gas velocity for all refrigerants. {industrial chillers may use 4000}
Systems with underground lines of 10 feet or more require a suction accumulator {size 50% of the total charge} and
& crankcase heaters. Insulate the vapor line minimum 1/2 in and encase within PVC per underground guidelines.
Applications may avoid the use of double risers by reducing the SL one size going up the riser and upsize at the top
to the correct SL size. You will sacrifice a little in capacity vs economics
Rule of thumb is to size hot gas bypass line same size as the liquid line. Insulate with minimum 1/2 wall insulation
|  | Commercial |  | RESIDENTIAL
We typically do not use double risers on systems up to 50 ton
Down sizing the suction riser line and sacrificing a little capacity is an option
Each job stands on its own and their are exceptions phone a friend
NOTE: These guidelines apply to JCI Systems
up to 50 ton.Larger York Applied units refer to the Applied
Piping Application Guide or call the
Application Hot line
Note: R410a does not require P traps on suction risers as POE oil is miscible with R410a. The key is to have enough velocity to ensure
the oil returns with thet R410a refrigerant
Split System heat pumps are required to use factory
matched AHRI rated Air Handlers/coils.
No 3rd party air handlers allowed including York Solutions
and Pipe lengths limited to 75 feet unless approved by
Application or Technical Service department no exceptions
Ounces per foot R410a Line Charge
Suction Line
Oz per foot
Liquid Line
Oz per foot
1/2 OD
0.003
1/4 OD
0.19
5/8 OD
0.064
5/16 OD
0.34
3/4 OD
0.08
3/8 OD
0.54
7/8 OD
0.128
1/2 OD
1
1 1/8 OD
0.208

## Series 20 AC & HP Physical Data
| Air Conditioning Condensing Units | Air Handler information shown below
If using a Norman AHRI rated System J07 to J25YCC and YDC Condensing units
Matched up with a Norman AH J07 to J25ND the Refrigeration Specialties are factory
installed and wired in the Air Handler along with a HGB Tee
Field wire back to Condensing per IOM
NOTE: J07YCC Condensing unit is One Stage Cool and requires a One Circuit
One Distributor Coil. Do not apply to a 2 distributor Coil.
NOTE: J10 thru J25YCC and YDC always match up with an Interlaced 50/50 2 Circuit
2 Distributor Coil
Important: JCI manufacturers one CU model with a factory installed Rawal Valve
J25YCC00A4BRW1 460-3 with disconnect. No other factory installed options or voltages
You will have to type the model into UST and the MLP will show up. A Submittal will
have to be made with a standard CU and Disconnect and add into the Submittal
the CU will have a factory installed Rawal Valve 460-3 PH with Disconnect ONLY
Heat Pump Condensing Units matched and Sold only with UPG AHRI Rated Air Handlers |  |  | Johnson Controls AHRI rated Air Handler
Johnson Controls AHRI rated Air Handler

## Series 40 Physical Data
Important: If you have to select a 2 circuit 2 Distributor Coil due to physical size
matched with a J30 and J40 CU always SQ and order the Solutions Coil with a 25%
Turn Down orifice in each Distributor. This will ensure you have the proper velocity of
Refrigerant under low load conditions. 2 Circuit 4 Distributors is preferred.
If applying to a Solutions Coil it is desirable to match up with a coil having {4} Distributors
Interlaced 2 circuit 50/50 or row split.
You must have full coverage of coil with all 4 stages
When applied to a 4 distributor coil and 4 TXV's, Solenoids etc the sequence of operation
is the same as shown in the Series 40 Installation Manual.
When applied to a 2 distributor coil and 2 TXV, Solenoids etc the sequence of operation
is not the same as shown in the Series 40 Installation Manual
If refrigerant lines are over 125 feet you will need to supply {2} Oil Separators.
Preferred OS's are Temprite Coascent style. Call Application or Technical Service Dept
If refrigerant lines are over 125 feet you may need to supply {2} Suction Accumulators.
Call Application or Technical Service Dept
If Indoor Coil is above the Condensing Unit you may need a LL Check Valve in each circuit
after the LL Service Valve on condensing Unit. You may also need a check valve on the
Hot Gas Bypass line at the bottom of the vertical lift to pevent damage to compressor
If applying a Solutions Coil with a J50YD Condensing Unit you must match up with a
2 Circuit Coil with 4 Distributors See piping diagram
If using a Norman AHRI rated System {J30 40 and 50YDC with a Matched
Norman AH J30 40 or 50ND the Refrigeration Specialties are factory installed and wired
in the Air Handler {{4} TXV's, {4} Solenoids HGB Tee and Transformer to power Solenoids
Field wire back to Condensing per IOM.

## Rawal Valves
Air Conditioning installation only. See separate instructions for Heat Pump Applications
APR Rawal Valves are sized by Performance along with actual Suction Line size

## TXV's
THERMOSTATIC EXPANSION VALVES
Source One PN | R410A | * See note below
Use these TXV's on Largo Fan Coils when matching up to a
S1-151365 | RCZE-2-GA Sporlan TXV 2 Tons 3/8 X 1/2 ODF R410A* | York UPG Condensing Unit. Order CU with Hard Start Kit
S1-151366 | RCZE-3-GA Sporlan TXV 3 Tons 3/8 X 1/2 ODF R410A | when using 208-230-1 PH CU's
S1-151368 | RCZE-4-GA Sporlan TXV 1/2 X 1/2 ODF R410A
S1-151492 | RCZE-5-GA Sporlan TXV1/2 X 1/2 ODF R410A
S1-168794 | ERZE-6-GA Sporlan TXV 1/2 4 X 5/8 ODF R410A | Nominal 6 ton capacity
S1-168719 | ERZE-8-GA Sporlan TXV 5/8 X 7/8 ODF R410A | Nominal 8 ton capacity use this on 7.5 ton circuits
S1-168802 | ERZE-12-1/2-GA Sporlan TXV 5/8 X 1 1/8 ODF R410A | Nominal 12.5 ton capacity use this size on 10 / 12.5 ton circuits
S1-168720 | ERZE-15-GA Sporlan TXV 5/8 X 1 1/8 ODF R410A | Nominal 15 ton capacity
S1-125396 | OZE-20-GA Sporlan TXV 7/8 X 1 1/8 ODF R410A | Nominal 20 ton capacity
Sporlan Application Hotline 636-392-3910
Largo DX Fan Coils can use the RCZE TXV's
* If the Largo Fan Coil is a one circuit DX coil the factory installs an Orifice. Do not use both metering devices. If the job
requires a TXV remove the orifice and install the TXV sized appropriately.
*2 Circuit DX Coils have one Distributor and require a TXV sized appropriately {1,5T use a 2 ton - 2.5 use a 3 ton etc}
208-230-1 PH Condensing must have a hard start kit when used with a TXV or have a scroll compressor.

## Solenoid and Sight Glasses
Source One PN
Must select correct 24v coil for ea solenoid
S1-310325 | COIL for below solenoids MKC-1,24V/50-60HZ,10W
S1-311710 | COIL for below solenoids requiring MKC-2,24V/50-60HZ,10W
S1-3310-00 | ME6S130-HP 3/8 ODF, Less MKC-1 COIL Manual Stem recommended** Note: Uses MKC-1 Coil
S1-4076-00 | ME6S140-HP 1/2 ODF, Less MKC-1 COIL Manual Stem recommended Note: Uses MKC-1 Coil
S1-3394-00 | ME9S240-HP 1/2 ODF, Less MKC-2 COIL Manual Stem recommended
S1-3500-00 | ME10S250-HP 5/8 ODF Less MKC-2 Coil Manual Stem recommended
S1-3524-00 | ME14S250-HP 5/8 ODF, Less MKC-2 COIL Manual Stem recommended
S1-3591-00 | ME19S270-HP 7/8 ODF, Less MKC-2 COILManual Stem recommended
S1-4036-00 | ME25S290-HP 1-1/8 ODF, Less MKC-2 COIL Manual Stem recommended
S1-4079-00 | VLV,SOL,E5S130-HP,3/8 ODF,LESS COIL Note: uses MKC-1 Coil
S1-3233-00 | VLV,SOL,E6S130-HP,3/8 ODF,LESS COIL Note: uses MKC-1 Coil
S1-3402-00 | VLV,SOL,E9S250-HP 5/8 ODF,LESS COIL
S1-4033-00 | VLV,SOL,E9S240-HP,1/2 ODF,LESS COIL
S1-3525-00 | VLV.SOL,E10S240-HP 1/2 ODF,LESSCOIL
S1-4100-00 | VLV,SOL,E14S250-HP,5/8 ODF,LESS COIL
S1-4077-00 | VLV,SOL,E19S270-HP,7/8 ODF,LESS COIL
S1-4101-00 | VLV,SOL,E2S120-HP,1/4 ODF,LESS COIL
24v Coil not included with above solenoids
S1-700052 |  | SA-12S Sight Glass 1/4 ODF
S1-700130 |  | SA-13S Sight Glass 3/8 ODF
S1-700299 |  | SA-14S Sight Glass 1/2 ODF
S1-700416 |  | SA-15S Sight Glass 5/8 ODF
S1-700507 |  | SA-17S Sight Glass 7/8 ODF |  | S1-SV-700598 1 5/8 Sight Glass
S1-700546 |  | SA-19S Sight Glass 1 1/8 ODF
Sporlan Application Hotline is 636-392-3910
Manual Stem solenoids allow installer/service tech to manually open the solenoid without electricity to unit

## Driers
LIQUID LINE SEALED DRIERS |  | Liquid Line Core Driers **
S1-400503 | C-083S 3/8 ODF LL Drier 8 cubic in
S1-401021 | C-163S 3/8 ODF LL Drier 16 cu in | S1-402082 | C-485-G LL Core Drier 5/8 ODF Less Core
S1-401023 | C-164S 1/2 ODF LL Drier 16 cu in | S1-402109 | C-487-G LL Core Drier 7/8 ODF Less Core
S1-401035 | C-165S 5/8 ODF LL Drier 16 cu in | S1-402152 | C-489-G LL Core Drier 1 1/8 ODF Less Core
S1-401305 | C-303S 3/8 ODF LL Drier 30 cu in | S1-402159 | C-4811-G LL Core Drier 1 3/8 ODF Less Core
S1-401307 | C-304S 1/2 ODF LL Drier 30 cu in | Larger tonnage core driers purchase locally
S1-401449 | C-305S 5/8 ODF LL Drier 30 cu in
S1-401313 | C-306S 3/4 ODF LL Drier 30 cu in | S1-404360 | RC-4864 Standard Cores*
S1-401505 | C-307S 7/8 ODF LL Drier 30 cu in | S1-404380 | RC-4864HH Clean up Charcoal Burn Out Core
S1-401317 | C-309S 1 1/8 ODF LL Drier 30 cu in | S1-404401 | RW-48 Clean up High Water Capacity Core
S1-401609 | C-414S 1/2 ODF LL Drier 41 cu in
S1-401610 | C-415S 5/8 ODF LL Drier 41 cu in | * Recommended to run system for a few days and replace cores
S1-52636217000 | C-417S 7/8 ODF LL Drier 41 cu in
S1-401618 | C-419S 1 1/8 ODF LL Drier 41 cu in
S1-401865 | C-609S 1 1/8 ODF LL Drier 60 cu in
HEAT PUMP SEALED BI-FLOW DRIERS
S1-404201 | HPC-163-S-HH 3/8 ODF Bi Flow Drier | ** Requires a 3 ball valve bypass to change cores without
S1-404241 | HPC-164-S-HH 1/2 ODF Bi Flow Drier | recovering the refrigerant. Larger tonnage sizes available
S1-404281 | HPC-165-S-HH 5/8 ODF Bi Flow Drier
S1-401372 | HPC-305-S-HH 5/8 ODF Bi Flow Drier
S1-401373 | HPC-307-S-HH 7/8 ODF Bi Flow Drier
Smaller sizes available
Sporlan Application Hotline 636-392-3910

## Ball Valve and Check Valves
BALL VALVES and CHECK VALVES
Source One PN
S1-502031 | EBV-1030, 3/8 ODF Ball Valve Sweat |  | Required on Heat Pump Applications when
S1-502033 | EBV-1040, 1/2 ODF Ball Valve Sweat |  | Coil is above Condensing unit
S1-502035 | EBV-1050, 5/8 ODF Ball Valve Sweat
S1-502039 | EBV-1070, 7/8 ODF Ball Valve Sweat
S1-502041 | EBV-1090, 1 -1/8 ODF Ball Valve Sweat
S1-SV-502029 | EBV-1020 | 1/4 Ball Valve
S1-502037 3/4 OD Ball Valve
NOTES: Split Systems
Series 20 Air Conditioning only* Condensing Units 7.5 to 25 ton come standard with factory installed check valves before each LL Service Valve
Units with Micro Channel condensers do not have the pump down capacity and refrigerant could ultimately migrate to the head of compressor
Check Valve prevents this.
Note: Hot Gas Bypass: If coil is above condensing unit always install a check valve on the bottom of the HGB line riser.
Series 40 Splits 30 to 50 Ton may require a field supplied and installed check valve on each LL circuit if Coil is above Condensing Unit as
these units use a copper tube aluminum fin condenser
* Series 20 Heat Pump Condensing Units use copper tube aluminum fin condensers. See above drawing
* Series 40 30, 40 and 50 Ton Condensing Units useCopper Tube Aluminum fin Condensers. CTAF

## Accumulators
SUCTION ACCUMULATORS
Intercept and temporarily store liquid refrigerant from the suction line
before it can reach the compressor* and cause damage. Size for 50% of the
total refrigerant charge in each circuit {4 pipe units require 2 Accumulators}.
Required on each circuit when piping is underground 10 feet or more
Required on line sets over 120 feet
Required at times when Coil is above Condensing Unit Call Application Dept
Fitting size should be the same size as the suction line pipe and not
necessarily the same size as the service valve.
* Compressors pump vapor refrigerant and not liquid
Source One does not stock this brand Purchase locally or an equal