## Parameters
Max measured length is 200', max equivalent length is 250'
Liquid Lines
Velocity
This should be between 100 fpm and 400 fpm for either R-410A or R-22.
Exceeding 400 fpm is acceptable, but may lead to refrigerant noise issues.
5 ton units using 3/8" lines will be 405 fpm for R-22 or 483 fpm for R-410A. While
acceptable, the possibility of noise must be understood and explained to the owner.
Avoid placing lines inside walls or directly above sleeping areas whenever possible.
Pressure Drop
This can be no more than 35 psi for R-22 or 60 psi for R-410A. Exceeding those
parameters is NOT ALLOWED as it would cause a loss of subcooling which leads
to capacity loss and/or failed components.
If a HP system has both vertical rise and vertical drop in the liquid line, enter the NET
value as a rise. In an A/C system enter the net rise OR net drop as appropriate
Suction Lines
Velocity
This should be between 1000 fpm and 3000 fpm for either R-410A or R-22.
Less than 1000 fpm on vertical risers may not allow oil to be returned to the
compressor and exceeding 3000 fpm will cause noise and vibration problems.
Velocity on horizontal runs is allowed to be as low as 800 fpm.
Pressure Drop
This should be no more than 3 psi for R-22 or 5 psi for R-410A
Exceeding these values is not recommended but is allowed. However it results in
capacity loss at a rate of 1% for every psi on R-22 and .7% for every psi on R-410A.
Long Line Sets
A long line set is defined as exceeding 75 Feet in length and MUST include a:
* crankcase heater if one is not factory installed.
* normally closed solenoid valve installed in the liquid line near the condensing unit.
* Non Bleed TXV (standard requirement on most units at 13 SEER and higher).
* hard start kit (single phase units only).
* Install Schrader access valves at the indoor unit for both the suction and liquid lines. These
are optional, but recommended to aid in troubleshooting pressure drops, subcooling and TXV operation
Using Receivers to overcome loss of subcooling
When using a receiver it must be understood that subcooling measurements cannot
be attempted in the field as the receiver contents are in a saturated state. No hydrolic or
hydorstatic seal exists so subcooling cannot be measured. A sight glass between the
receiver and TXV must be used to charge the system by adding refrigerant until bubbles are gone,
then adding 1/2 the pump down capacity of the receiver. Use of receivers is not supported by the
factory because the application typically does not fall within their published guidelines.
NOTES:
If on a long line set the liquid line will be exposed to direct sunlight, or very high ambient conditions, it should be insulated.
If the unit contains a rotary compressor the MAXIMUM line length is 100'
If more than 5 feet of underground piping is installed on a cooling only system, install an accumulator with volume equal to 1/2 the system's refrigerant volume.
If a long line set application uses a two stage system, meaning a single refrigerant circuit with either two compressors or a single compressor that reduces capacity, consider decreasing the vertical suction riser (if one exists) by one line size.
Noise from lines running through basements and/or attics can often be avoided by adhearing to the velocity guidelines and taking care use non metalic hangers such as mesh strap which insulates the refrigerant lines from the joists. Overcharging will also contribute to noise. Discharge or vapor line mufflers can eliminate harmonic noises sometimes encountered in otherwise properly sized and charged systems.
For addtional information consult the most recent Application Guidlines for Refrigeration Piping as published by UPG. If your application exceeds these
parameters, you must contact Jack Bartell or the factory for assistance

## Main
Ref Pipe Sizing (Each time you start the program or change refrigerants, click in cell C27 to refresh)
Note: If the unit has dual refrigeration lines, meaning two indepentant refrigeration systems, only input 1/2 the unit tonage | [8 empty] | ver 2.21.11
* Fields marked with a red asterick require input and must be changed or checked for each line sizing job
Date | 2026-07-30
Unit Model # |  |  |  | Requested By
Distributor Name |  |  |  | Prepared By
Liquid Leaving OD Unit |  |  |  | Entering ID Unit |  |  | Tolerance or Detail
Factory Charge OD Unit (lbs-oz) | 0 | 0 |  |  |  |  | See parameter sheet if values are exceeded
Coil Adder for system match (oz) | 0 |  |  | Liquid Line Velocity | 290.0265 | FPM | Recommended maximum is 400
Refrigerant Type | R410A | * |  | LL Pressure Drop | 1.9346 | lbs | R22 Below 35, R410A Below 60
Unit Size in Tons | 3 | *
|  |  |  | Mass Flow | 504.7933 | lbs/hr
|  |  |  | Temp at ID | 110.058 | F
Liquid Line Size | 0.375 | * |  | Pressure at ID | 442.5654 | psig
NET Vertical Rise ft | 0 | * |  | Subcooling @ OD | 15 |  | Should be above 5
NET Vertical Drop ft | 0 | * |  | Subcooling @ ID | 14.614 |  | Should be above 5
Elbows | 6 | *
Total Line Length ft | 15 | *
Liquid Line Temp F | 110 |  |  | Total Liquid Line Charge | 7.8306 | oz | Refrigerant charge for Liquid Line Only
Liquid Line Pressure PSIG | 444.5 |  |  | LL Charge (minus 15 ft) | 0 | oz | LL charge minus the 15' length included by the factory
Ambient Surrounding Liquid Line | 110 |  |  | Suction Line Charge | 1.2996 | oz | Refrigerant charge for Suction Line Only
OD Ambient Temp F | 105 |  |  | SL Charge (minus 15 ft) | 0 | oz | SL charge minus the 15' length included by the factory
Click for default Values based on OD ambient |  |  |  | Total System Charge | 0 | oz | LL, SL, plus OD & Coil adder values from B10 & B11
|  |  |  | Additional Charge Req'd | 0 | oz | LL, SL values (minus 15'), plus coil adder from B11
Suction Line Calculations
Refrigerant Type | R410A |  |  | Total SL Pressure Drop | 1.2375 | lbs | R22 Below 3, R410A Below 5
Unit Size in Tons | 3 |  |  | Suction Line Velocity | 1761.4929 | FPM | Between 1000 and 3000 (800 on horizontal section)
Suction Line Size | 0.75 | *
Elbows | 6
Suction Line Length | 15
Click to print with piping tables
Yellow cells are optional inputs for total charge calculations and/or text fields
Dark Green cells are inputs that must be entered for each job
Blue cells are rarely used options for extreme applications
Lighter green cells are calculated or carried values, not used for inputs
Suction Line Pressure Drop Calc
For Multiple Stage Applications
[9 empty] | Reduced | Full
[8 empty] | Horizontal Section | 0 | 0
[8 empty] | Vertical Section | 0 | 0
[8 empty] | Total P. Drop | 0 | 0
R-22 Liquid Line | VERT. HT |  |  | TOTAL | UNIT | FRICTION | TOTAL | LIQ. | LIQ | Liq line
LINE | + DROP | NUMBER | ACT. | EQU. | SIZE | LOSS | PRESS | LINE | LINE | -15 ft
SIZE | - RISE | ELBOWS | length | length | MBH | PSI | LOSS | CHARGE | VEL | Ounces
0.25 | 0 | 6 | 15 | 19.2 | 36 | 22.1491 | 22.1491 | 3.45 | 650.2 | 0
0.3125 | 0 | 6 | 15 | 19.8 | 36 | 5.148 | 5.148 | 6 | 380.1 | 0
0.375 | 0 | 6 | 15 | 20.4 | 36 | 1.9346 | 1.9346 | 9.3 | 242.7 | 0
0.5 | 0 | 6 | 15 | 43.2 | 36 | 0.912 | 0.912 | 16.8 | 126.96 | 0
0.625 | 0 | 6 | 15 | 49.2 | 36 | 0.31568 | 0.31568 | 27.15 | 79.02 | 0
0.75 | 0 | 6 | 15 | 54 | 36 | 0.13749 | 0.13749 | 40.05 | 52.92 | 0
0.875 | 0 | 6 | 15 | 61.8 | 36 | 0.068495 | 0.068495 | 56.1 | 38.1 | 0
1.125 | 0 | 6 | 15 | 31.2 | 36 | 0.0092549 | 0.0092549 | 93.6 | 22.34 | 0
1.375 | 0 | 6 | 15 | 34.2 | 36 | 0.0035265 | 0.0035265 | 142.35 | 14.67 | 0
1.625 | 0 | 6 | 15 | 37.8 | 36 | 0.0016552 | 0.0016552 | 200.85 | 10.36 | 0
2.125 | 0 | 6 | 15 | 46.2 | 36 | 0.00054165 | 0.00054165 | 350.64 | 5.96 | 0
R22 Suction Line |  |  | TOTAL | UNIT | FRICTION |  | SUCT. | Suc Line
LINE | NO. | ACT. | EQU. | SIZE | LOSS | REF. | LINE | -15 ft
SIZE | ELBOWS | length | length | MBH | PSI | VELOCITY | CHARGE | CHARGE OZ.
0.5 | 6 | 15 | 22.2 | 36 | 12.7083 | 5910 | 0.3 | 0
0.625 | 6 | 15 | 24 | 36 | 4.624 | 3675 | 0.6 | 0
0.75 | 6 | 15 | 24.6 | 36 | 1.6975 | 2498.5714 | 0.9 | 0
0.875 | 6 | 15 | 25.8 | 36 | 0.80221 | 1767 | 1.2 | 0
1.125 | 6 | 15 | 29.4 | 36 | 0.25139 | 1032 | 2.1 | 0
1.375 | 6 | 15 | 29.4 | 36 | 0.088752 | 684 | 3.12 | 0
1.625 | 6 | 15 | 29.4 | 36 | 0.037428 | 480 | 4.5621 | 0
2.125 | 6 | 15 | 29.4 | 36 | 0.0095516 | 270 | 8.4 | 0
2.625 | 6 | 15 | 29.4 | 36 | 0.0033223 | 180 | 12.48 | 0
3.125 | 6 | 15 | 29.4 | 36 | 0.0014535 | 132 | 18.24 | 0
3.625 | 6 | 15 | 29.4 | 36 | 0.00010714 | 126 | 24.72 | 0
4.125 | 6 | 15 | 29.4 | 36 | 4.8048e-05 | 67.5 | 32.4 | 0
R410A Liquid Line | VERT. HT |  |  | TOTAL | UNIT | FRICTION | TOTAL | LIQ. | LIQ | Liq line
LINE | + DROP | NUMBER | ACT. | EQU. | SIZE | LOSS | PRESS | LINE | LINE | -15 ft
SIZE | - RISE | ELBOWS | length | length | MBH | PSI | LOSS | CHARGE OZ. | VEL | Ounces
0.25 | 0 | 6 | 15 | 19.2 | 36 | 22.1491 | 22.1491 | 2.9049 | 776.989 | 0
0.3125 | 0 | 6 | 15 | 19.8 | 36 | 5.148 | 5.148 | 5.052 | 454.2195 | 0
0.375 | 0 | 6 | 15 | 20.4 | 36 | 1.9346 | 1.9346 | 7.8306 | 290.0265 | 0
0.5 | 0 | 6 | 15 | 43.2 | 36 | 0.912 | 0.912 | 14.1456 | 151.7172 | 0
0.625 | 0 | 6 | 15 | 49.2 | 36 | 0.31568 | 0.31568 | 22.8603 | 94.4289 | 0
0.75 | 0 | 6 | 15 | 54 | 36 | 0.13749 | 0.13749 | 33.7221 | 63.2394 | 0
0.875 | 0 | 6 | 15 | 61.8 | 36 | 0.068495 | 0.068495 | 47.2362 | 45.5295 | 0
1.125 | 0 | 6 | 15 | 31.2 | 36 | 0.0092549 | 0.0092549 | 78.8112 | 26.6963 | 0
1.375 | 0 | 6 | 15 | 34.2 | 36 | 0.0035265 | 0.0035265 | 119.8587 | 17.5307 | 0
1.625 | 0 | 6 | 15 | 37.8 | 36 | 0.0016552 | 0.0016552 | 169.1157 | 12.3802 | 0
2.125 | 0 | 6 | 15 | 46.2 | 36 | 0.00054165 | 0.00054165 | 295.2389 | 7.1222 | 0
R410A Suction Line |  |  | TOTAL | UNIT | FRICTION |  | SUCT. | Suc Line
LINE | NO. | ACT. | EQU. | SIZE | LOSS | REF. | LINE | -15 ft
SIZE | ELBOWS | length | length | MBH | PSI | VELOCITY | CHARGE OZ. | CHARGE OZ.
0.5 | 6 | 15 | 22.2 | 36 | 9.2644 | 4166.55 | 0.4332 | 0
0.625 | 6 | 15 | 24 | 36 | 3.3709 | 2590.875 | 0.8664 | 0
0.75 | 6 | 15 | 24.6 | 36 | 1.2375 | 1761.4929 | 1.2996 | 0
0.875 | 6 | 15 | 25.8 | 36 | 0.58481 | 1245.735 | 1.7328 | 0
1.125 | 6 | 15 | 29.4 | 36 | 0.18326 | 727.56 | 3.0324 | 0
1.375 | 6 | 15 | 29.4 | 36 | 0.0647 | 482.22 | 4.5053 | 0
1.625 | 6 | 15 | 29.4 | 36 | 0.027285 | 338.4 | 6.5877 | 0
2.125 | 6 | 15 | 29.4 | 36 | 0.0095516 | 190.35 | 12.1296 | 0
2.625 | 6 | 15 | 29.4 | 36 | 0.0024219 | 126.9 | 18.0211 | 0
3.125 | 6 | 15 | 29.4 | 36 | 0.0010596 | 93.06 | 26.3386 | 0
3.625 | 6 | 15 | 29.4 | 36 | 7.8108e-05 | 88.83 | 35.6957 | 0
4.125 | 6 | 15 | 29.4 | 36 | 3.5027e-05 | 47.5875 | 46.7856 | 0
R22 | 1 |  | 0.25
R410A | 1.5 |  | 0.3125 | 0
0 | 2 |  | 0.375 | 0.375
0 | 2.5 |  | 0.5 | 0.5
| 3 |  | 0.625 | 0.625
Btu loss per 1 percent of capacity | 3.5 |  | 0.75 | 0.75
#VALUE! | 4 |  | 0.875 | 1
| 5 |  | 1.125
| 6.5 |  | 1.375
| 7.5 |  | 1.625
Needs TXV | 8.5 |  | 2.125
Recommend Accumulator and CCH | 10 |  | 2.625
Add Suction Line Trap at bottom of riser | 12.5 |  | 3.125
Add Inverted Suction Line Trap at top of riser | 15 |  | 3.625
| 20 |  | 4.125
Accumulator needs Resizing to 50% of total charge | 25
30
40
REMEMBER: With 2 stage units you must look at the suction line velocity at reduced capacity to insure velocity remains above 1000fpm on suction risers. If it does not, reducing the riser size by one size will correct the problem

## Calcs (hidden)
Specific Heat cp
Viscosity BTM | 0.313
Viscosity TOP | 0.332
TEMPERATURE BTM | 100
TEMPERATURE TOP | 120
X-TEMP | 0.5
Viscosity | 0.3225
|  |  | Picks from insulated or not | #REF!
BARE COPPER |  |  | INSULATED COPPER
AMBIENT TEMP | 110 | oF | AMBIENT TEMP | 0 | oF
LIQUID TEMP | 110 | oF | LIQUID TEMP | #REF! | oF
TUBE DIAMETER | 0.375 | in | TUBE DIAMETER | 0.75 | in
LINE LENGTH | 15 | ft | LINE LENGTH | 15 | ft
QL | 9.45 | Btu/h | INSULATION THICKNESS | 0 | in
|  |  | QL | #REF! | Btu/h
[0.63+0.03*D0.75*Dt1.25+1.17*D*Dt]*L
D0.75 | 0.47921 |  | D0.75 | 0.80593
Dt | 0 |  | Dt | #REF!
Dt1.25 | 0 |  | Dt1.25 | #REF!
0.03*D0.75*Dt1.25 | 0 |  | Th-0.33 | #NUM!
1.17*D*Dt | 0 |  | 0.06*D0.75*Dt1.25 | #REF!
TEMPERATURE AT LIQUID LINE
Liquid Temp In | 110 | oF
Cp | 0.3225 | Btu/(lb*h) | BARE COPPER
Mass Flow | 504.7933 | lbs/h
Liquid Temp Out | 110.058 | oF | AMBIENT TEMP | 0 | oF
|  |  | LIQUID TEMP | #REF! | oF
|  |  | TUBE DIAMETER | 0.75 | in
|  |  | LINE LENGTH | 15 | ft
|  |  | QL | #REF! | Btu/h
[0.63+0.03*D0.75*Dt1.25+1.17*D*Dt]*L
|  |  | D0.75 | 0.80593
|  |  | Dt | #REF!
|  |  | Dt1.25 | #REF!
|  |  | 0.03*D0.75*Dt1.25 | #REF!
|  |  | 1.17*D*Dt | #REF!

## Refrigerant (hidden)
Temp | Viscosity | Thermal Conductivity | Specific Heat
-100 | 1.153 | 0.0789 | 0.255
-80 | 1.002 | 0.0757 | 0.256
-60 | 0.883 | 0.0725 | 0.259
-40 | 0.788 | 0.0693 | 0.262
-20 | 0.71 | 0.0661 | 0.266
0 | 0.646 | 0.063 | 0.271
20 | 0.592 | 0.0598 | 0.276
40 | 0.546 | 0.0566 | 0.286
60 | 0.507 | 0.0534 | 0.291
80 | 0.474 | 0.0502 | 0.3
100 | 0.444 | 0.0471 | 0.313
120 | 0.422 | 0.0439 | 0.332
140 | 0.387 | 0.0407 | 0.357
160 | 0.34 | 0.0371 | 0.39
180 | 0.285 | 0.0318 | 0.433
190 | 0.244 | 0.0288
200 | 0.182 | 0.0238
205 | 0.074 | 0.0177
Pressure Enthalpy R-22 |  |  | Pressure Enthalpy of R410A |  |  | Entering Liquid Line
[7 empty] | 444.5 |  |  | 444.5
Pressure | Enthalpy | Temp | Pressure | Enthalpy | Temp | PSIG | Enth | Temp |  | PSIG | Enth | Temp
150.7 | 34 | 83 | 201.5 | 39.9 | 70 | 405.4 | 52.5 | 155 |  | 444.5 | 64.2 | 125
160.6 | 35.2 | 87 | 218.2 | 41.9 | 75 | 405.4 | 52.5 | 155 |  | 474 | 66.9 | 130
171 | 36.5 | 91 | 235.9 | 43.9 | 80
181.7 | 37.7 | 95 | 254.6 | 46 | 85 |  | #DIV/0! | #DIV/0! |  |  | 64.2 | 125
193 | 39 | 99 | 274.3 | 48.1 | 90 | R-22 |  |  |  | R410A
201.7 | 39.9 | 102 | 295 | 50.2 | 95 | Lvg Liquid Line
213.8 | 41.2 | 106 | 316.9 | 52.4 | 100 |  | 442.5654 |  |  | 442.5654
223.1 | 42.1 | 109 | 339.9 | 54.6 | 105
236 | 43.4 | 113 | 364.1 | 56.9 | 110 | 405.4 | 52.5 | 155 |  | 444.5 | 64.2 | 125
246 | 44.4 | 116 | 389.6 | 59.3 | 115 | 405.4 | 52.5 | 155 |  | 474 | 66.9 | 130
256.3 | 45.4 | 119 | 416.4 | 61.7 | 120
266.9 | 46.4 | 122 | 444.5 | 64.2 | 125 |  | #DIV/0! | #DIV/0! |  |  | 64.0229 | 124.6721
274.2 | 47 | 124 | 474 | 66.9 | 130 | R-22 |  |  |  | R410A
289.1 | 48.4 | 128 | 505 | 69.7 | 135
304.5 | 49.7 | 132 | 537.9 | 72.8 | 140
320.6 | 51.1 | 136 | 571.7 |  | 145
337.2 | 52.5 | 140 | 607.6 |  | 150
359.1 |  | 145 | 645.2 |  | 155
381.7 |  | 150
405.4 |  | 155
[6 empty] | LL @ ID | 110.058 |  |  | LL @ ID | 110.058
[6 empty] | SC @ ID | #DIV/0! |  |  | SC @ ID | 14.614
[6 empty] | Enth @ ID | #DIV/0! |  |  | Enth @ ID | 58.3544
[6 empty] | SC @ OD | #DIV/0! |  |  | SC @ OD | 15
[6 empty] | Enth @ OD | #DIV/0! |  |  | Enth @ OD | 58.0229
0.3 | btus/lb subcooled |  | 0.4 | btus/lb subcooled
[6 empty] | default pressure R22 |  |  |  | default pressure R410A
Temp | Enthalpy | Press | Temp | Enthalpy | Press | OD Temp | 105 |  |  | OD Temp | 105
83 | 34 | 150.7 | 70 | 39.9 | 201.5 | Sat Temp | 125 |  |  | Sat Temp | 125
87 | 35.2 | 160.6 | 75 | 41.9 | 218.2 | LL Temp | 110 |  |  | LL Temp | 110
91 | 36.5 | 171 | 80 | 43.9 | 235.9 | Sat Press | 277.925 |  |  | Sat Press | 444.5
95 | 37.7 | 181.7 | 85 | 46 | 254.6
99 | 39 | 193 | 90 | 48.1 | 274.3
102 | 39.9 | 201.7 | 95 | 50.2 | 295 |  | 125 |  |  | 125
106 | 41.2 | 213.8 | 100 | 52.4 | 316.9
109 | 42.1 | 223.1 | 105 | 54.6 | 339.9 | 124 | 52.5 | 274.2 |  | 125 | 64.2 | 444.5
113 | 43.4 | 236 | 110 | 56.9 | 364.1 | 128 | 52.5 | 289.1 |  | 130 | 66.9 | 474
116 | 44.4 | 246 | 115 | 59.3 | 389.6
119 | 45.4 | 256.3 | 120 | 61.7 | 416.4 |  | 52.5 | 277.925 |  |  | 64.2 | 444.5
122 | 46.4 | 266.9 | 125 | 64.2 | 444.5 | R-22 |  |  |  | R410A
124 | 47 | 274.2 | 130 | 66.9 | 474
128 | 48.4 | 289.1 | 135 | 69.7 | 505
132 | 49.7 | 304.5 | 140 | 72.8 | 537.9 | Default Liquid Line |  |  | Default Suction Line
136 | 51.1 | 320.6 | 145 |  | 571.7
140 | 52.5 | 337.2 | 150 |  | 607.6
145 |  | 359.1 | 155 |  | 645.2
150 |  | 381.7
155 |  | 405.4
[6 empty] | Temp | 110
[6 empty] | Press | 444.5 |  | Temp | 60
[6 empty] | Ambient | 110 |  | evap char

## Compressors (hidden)
Compressor Performance |  |  |  |  | Mass Flow
[5 empty] | Tons | Flow
[5 empty] | 1 | 168.2644
T (Suction/Evap) | 45 |  |  |  | 1.5 | 252.3966
T (Discharge/Cond) | 125 |  |  |  | 2 | 336.5289
[5 empty] | 2.5 | 420.6611
VARIABLE |  |  |  |  | 3 | 504.7933
CAPACITY | 23456.6842 |  |  |  | 3.5 | 588.9255
POWER | 1954.0652 |  |  |  | 4 | 673.0577
CURRENT | 8.6769 |  |  |  | 5 | 841.3221
MASSFLOW | 336.5289 |  |  |  | 6.5 | 1093.7188
[5 empty] | 7.5 | 1261.9832
| Rated Capacity | 22200 | H20J223 |  | 8.5 | 1430.2476
Constants |  |  |  |  | 10 | 1590.0698
| Capacity | Power | Current | Massflow | 12.5 | 1987.5872
Constant 1 | 10264.2568 | 487.1922 | -4.3261 | 67.3911 | 15 | 2385.1046
Constant 2 | 599.0189 | -4.8536 | 0.060201 | 6.0764 | 20 | 3180.1395
Constant 3 | 113.1001 | 9.9737 | 0.19674 | 2.4484 | 25 | 3975.1744
Constant 4 | 4.0171 | -0.40579 | -0.0024484 | 0.025078 | 30 | 4770.2093
Constant 5 | -1.9431 | 0.25666 | -5.1777e-05 | -0.0061082 | 40 | 6360.279
Constant 6 | -2.3304 | -0.019213 | -0.0012561 | -0.031641
Constant 7 | -0.0016161 | -0.0013718 | -3.095e-06 | -5.7753e-05
Constant 8 | 0.0036098 | 0.0034388 | 2.017e-05 | 0.0002753
Constant 9 | -0.0074033 | -0.00036566 | 2.2145e-06 | -0.00010711
Constant 10 | 0.0080618 | -0.00019024 | 2.1484e-06 | 9.1399e-05
VARIABLE
CAPACITY
POWER
CURRENT
MASSFLOW | 1590.0698
| Rated Capacity | 108000 | ZRT108K3-TF5
Constants
| Capacity | Power | Current | Massflow
Constant 1 |  |  |  | 474.6303
Constant 2 |  |  |  | 11.8689
Constant 3 |  |  |  | 7.6521
Constant 4 |  |  |  | 0.11331
Constant 5 |  |  |  | 0.073015
Constant 6 |  |  |  | -0.083484
Constant 7 |  |  |  | 0.00050196
Constant 8 |  |  |  | -5.1726e-05
Constant 9 |  |  |  | -0.00027942
Constant 10 |  |  |  | 0.00023189

## Application Guideline Tables
Tables imported from York's Application Guideline (247077-UAD-H-0209)